| THE MINISTRY OF HEALTH ----- | THE SOCIALIST REPUBLIC OF VIETNAM Independence - Freedom - Happiness -------- |
| --- | --- |
| No. 3733/2002/QD-BYT | Hanoi, October 10, 2002 |

DECISION

PROMULGATING 21 LABOR HYGIENE STANDARDS, 05 PRINCIPLES AND 07 LABOR HYGIENE MEASUREMENTS

THE MINISTER OF HEALTH

Pursuant to the Law on People’s health protection

Pursuant to the Government's Decree No. 68/CP of October 11, 1993 on defining the functions, tasks, powers and organizational structure of the Ministry of Health;

Upon obtaining the consent of the Ministry of Labor, War Invalids and Social Affairs in the Official Dispatch No. 941/LDTBXH-BHLD of April 02, 2002; Vietnam Chamber of Commerce and Industry in the Official Dispatch No. 0850/PTM-VPGC of April 17, 2002.

At the proposal of the Director of Defensive Medicine Department – the Ministry of Health

DECIDES:

Article 1. Promulgating together with this Decision:

1. Twenty one (21) Standards of labor hygiene applicable to facilities that employ workers.

2. Five (05)  principles and seven (07) measurements of labor hygiene being fundamental guidance for establishing working systems and positions, working machinery and tools, labor classification.

Article 2. This Decision takes effect after 15 days as from its promulgation. The provisions on labor hygiene from section 1 to section 8 in the fourth part “Provisions on labor hygiene” in the Decision No. 505-BYT/QD on April 13, 1992 of The Minister of Health on promulgating a number of Temporary hygiene standards are abolished.

Article 3. The Director of Defensive Medicine Department is responsible to organize, direct and inspect the implementation of this Decision.

Article 4. the Chief officers, the Chief Inspector, the Director of Defensive Medicine Department – the Ministry of Health, Heads of units affiliated to the Ministry of Health, the Directors of the Services of Health of central-affiliated cities and provinces are responsible to implement this Decision.

|  | FOR THE MINISTER OF HEALTH DEPUTY MINISTER Nguyen Van Thuong |
| --- | --- |

TWENTY ONE (21) STANDARDS, FIVE (05) PRINCIPLES AND SEVEN (07) MEASUREMENTS OF LABOR HYGIENE

(Promulgated together with the Decision No. 3733/2002/QD-BYT of The Minister of Health on October 10. 2002)

Part 1: Twenty one (21) standards of labor hygiene

1. Standards of hygienic amenities

2. Standards of hygienic distance

3. Manual labor – Standards of task classification by energy consumption

4. Manual labor – Standards of task classification by heart rate

5. Carrying standard – Limited weight

6. Standards of lighting

7. Standards of microclimate

8. Standards of silicon dust

9. Standards of non-silicon dust

10. Standards of cotton dust

11. Standards of asbestos dust

12. Standards of noise

13. Standards of vibration

14. Standards of static magnetic field - Magnetic flux density

15. Standards of low-frequency magnetic field - Magnetic flux density

16. Standards of low-frequency electromagnetic field intensity and static electric field

17. Standards of intensity of electromagnetic field from 30kHz - 300GHz

18. Ultraviolet radiation – Acceptable limits

19. Standards of radioactivity

20. X-ray radiation – Acceptable limit

21. Chemicals – Acceptable limits in the working air.

Part 2:  Five (05) principles and seven (07) measurements of labor hygiene

1. Principle 1 – Ergonomic design of labor systems

2. Principle 2 – Ergonomic design of labor positions

3. Principle 3 – Ergonomic design of machinery and tools

4. Principle 4 – Work area layout

5. Principle 5 – Work positions with computers

6. Measurement 1 – Work positions with computers

7. Measurement 2 – Height of work surfaces

8. Measurement 3 – Distance from eyes to things

9. Measurement 4 - View angle

10. Measurement 5 – Footrest

11. Measurement 6 – Lifting height

12. Measurement 7 – Physiological measurements of thermal strain - Limit values

Part 1

TWENTY ONE (21) STANDARDS OF LABOR HYGIENE

I. STANDARDS OF HYGIENIC AMENITIES

1. Scope of regulation: Specifying the number of hygienic amenities for workers.

2. Subjects of application: The facilities that employ workers (production facilities, business establishments, offices…)

3. Definition

The term is construed as follows:

- Hygienic amenities mean: The hygiene works and general amenities serving workers at facilities that employ workers.

4. Standards of hygienic amenities

| Hygiene facilities | Standard | Scope of application |
| --- | --- | --- |
| Latrine pit | By shift: 1- 10 people/pit 11- 20 people /pit 21 - 30 people /pit | Facilities with: 1- 100 people 101 - 500 people Over 500 people |
| Urinary pit | By shift: 1- 10 people /pit 11- 20 people /pit 21 - 30 people /pit | Facilities with: 1- 100 people 101 - 500 people Over 500 people |
| Bathroom | By shift: 1- 20 people /room 21- 30 people / room Over 30 people / room | Facilities with: 1- 300 people 301 - 600 people Over 600 people |
| Menstrual hygiene room | By shift: 1- 30 females/ room Over 30 females/ room | Facilities with: 1 - 300 people Over 300 people |
| Hand-washing faucet | By shift: 1 - 20 people / faucet 21 - 30 people / faucet Over 30 people / faucet | Facilities with: 1 - 100 people 101 - 500 people Over 500 people |
| Emergency clean water faucet | 1 - 200 people /faucet Over 200 people / faucet | Facilities with: 1 - 1,000 people Over 1,000 people |
| Clothes storing place | 1 person/slot, hook, or small locker. | Facilities employing workers (production facilities, business establishments, offices…) |
| Potable water | 1.5 liter/person/shift | Facilities hiring workers (production facilities, business establishments, offices…) |

II.  STANDARDS OF HYGIENIC DISTANCE

1. Scope of regulation: Minimum distance from the production facility to residential areas.

2. Subjects of application: These standards are applicable to facilities separately situated outside processing and exporting zones or industrial zones that emit toxic substances that harm the environment and human health.

3. Definition

The term is construed as follows:

- Standards of hygienic distance: is the minimum distance from the emission sources in the house, the producing facility or the technology line to residential areas.

4. Standards of hygienic distance:

4.1. Fuel

4.1.1. A distance of 1,000m for facilities:

a. Producing gas, lighting gas, vapor with production over 50,000 m3/hour.

b. Producing inflammable gas with production over 5,000 ton/year.

c. Conducting petroleum refinery and petrochemistry with over 0.5% sulphur.

d. Filtering and treating coal

e. Processing fuel slabs.

f. Producing semi-finished products being naphthalene with production over 2,000 ton/year.

g. Producing hydrocarbons by chloridization and hydrochloridization.

4.1.2. A distance of 500m for facilities:

a. Producing inflammable gas from fossil coal or peat with production from 5,000 – 50,000 m3/hour.

b. Processing fossil coal powder.

c. Conducting petroleum refinery and petrochemistry with production under 0.5% sulphur.

d. Producing acetylene from natural gas.

e. Producing inflammable gas with production from 1,000 to 5,000 m3/hour.

f. Processing fluoric gas.

g. Producing acetylene from hydrocarbide

4.1.3. A distance of 100m for facilities:

a. Producing inflammable gas from fossil coal or peat with production under 5,000 m3/hour.

b. Producing inflammable gas with production under 1,000 m3/year.

c. Producing matches

d. Producing compressed oxygen and hydrogen

e. Being fuel depots.

g. Selling petrol.

h. Storing inflammable and explosive materials.

4.2. Chemicals, fertilizers and rubber

4.2.1. A distance of 1,000m for facilities:

a. Producing nitrogen and nitrogenous fertilizer.

b. Producing industrial finished products being dye from benzene and ether with production over 1,000 ton/year.

c. Producing NaOH by electrolysis

d. Producing oil (benzol, toluene, xylol naphthol, phenol cresol, anthracene, phenantrol, acridine, carbazole)

e. Producing chloride rubber “nairit” in facilities that produce chlorine.

f. Producing synthetic ethyl ether.

g. Producing methyl ether and ethyl solution.

h. Producing synthetic chemicals.

i. Producing organic and inorganic acid

- Sulfuric acid.

- Hydrochloric acid

- Nitric acid

- Picric acid.

- Flavic, criolit and fluoric salt.

- Aminolenan.

- Xinhin.

j. Producing

- Mercury.

- Arsenic and inorganic compounds with arsenic.

- Chorine.

- Phosphorus.

- Corundum.

- Beryllium.

4.2.2. A distance of 500m for facilities:

a. Producing ammonia

b. Producing

- Niobium.

- Tantalum.

- Rare metal using chloridization.

- Baryum chloride using hydrosulphur.

- Industrial grease (hydrogenated by non-electrolyzing methods).

c. Producing products from asbestos.

d. Producing industrial semi-finished products being aniline paint from benzene and ether with production over 1,000 ton/year.

e. Producing polyethylene and polypropylene from petroleum gas.

f. Producing synthetic fatty acid.

g. Producing synthetic rubber.

h. Recycling rubber.

i. Producing rubber, ebonite and rubber paper.

j. Vulcanizing rubber using hydrosulfur.

k. Producing nicotine.

l. Producing phenol formaldehyde and other artificial powder with production over 300 ton/year.

m. Producing artificial mineral paint.

n. Vulcanizing rubber using hydrosulfur.

o. Recycling rubber.

p. Producing spray paint.

q. Producing, processing, packing, preserving plant protection chemicals.

r. Producing phosphate and superphosphate.

s. Producing soap with production over 2,000 ton/year.

4.2.3. A distance of 100m for facilities:

a. Producing glycerine.

b. Producing natural rubber.

c. Producing shoe rubber without using dusty soluble organic substances.

d. Producing plastic being polyvinyl chloride, vinyl, polyurethane foam, spongy plastic, plastic glass, spyropo.

e. Producing perfume.

f. Vulcanizing rubber without using sulfurcarbon.

g. Producing artificial gems.

h. Producing plastic products or processed from semi-finished plastic materials.

i. Producing soap with production under 2,000 ton/year.

j. Producing products from synthetic powder, polymer and plastic using various methods.

4.3. Ferrous metallurgy

4.3.1. A distance of 1,000m for facilities:

a. Producing magnesium (Chloridizing method).

b. Refining cast iron that the total capacity of the blast furnaces is over 1,500 m3.

c. Producing aluminum by electrolysis

d. Refining steel using open-hearth furnace method and transitional furnace with production over 1,000,000 ton/year.

e. Producing ferrous alloy.

4.3.2. A distance of 500m for facilities:

a. Producing magnesium (by non-chloridizing method).

b. Refining cast iron that the total capacity of the blast furnaces from 500 to 1,500 m3.

b. Producing cast iron pipe with production over 10,000 ton/year.

d. Refining steel using open-hearth furnace method, electric furnace and transitional furnace with production under 1,000,000 ton/year.

e. Producing lead-sheathed cable insulated rubber-sheathed cable

4.3.3. A distance of 100m for facilities:

a. Producing bare cable.

b. Processing cast iron, steel with production under 10,000 ton/year.

c. Producing metal electrodes.

4.4. Non-ferrous metallurgy

4.4.1. A distance of 1,000m for facilities:

b. Re-processing non-ferrous metal with production over 3,000 ton/year.

b. Refining non-ferrous metal directly from ore and refined ore.

c. Burning non-ferrous metal ore and burned piryte.

4.4.2. A distance of 500m for facilities:

a. Producing non-ferrous metal with production over 2,000 ton/year.

b. Re-processing non-ferrous metal with production from 1,000 to 3,000 ton/year.

c. Producing zinc, copper, nickel, cobalt by electrolyzing solvent with water.

4.4.3. A distance of 100m for facilities:

a. Producing antimony by electrolysis.

b. Plating with zinc, chrome, nickel

4.5. Building material

4.5.1. A distance of 1,000m for facilities:

a. Producing porland cement, porland slag cements, puzolan cement with production over 150,000 ton/year.

b. Producing magnesite lime, dolomitic lime and samot lime using spinning furnace or other kinds of furnaces except for manual furnace.

4.5.2. A distance of 500m for facilities:

a. Producing porland cement, porland slag cements, puzolan cement with production under 150,000 ton/year.

b. Producing plaster.

c. Producing building materials (stones, sand, gravel).

d. Producing local cement with production under 5,000 ton/year.

e. Producing magnesite lime, dolomitic lime using manual furnaces.

f. Producing concrete, asphalt.

g. Producing glass wool and slag wool.

h. Producing asphalt paper.

4.5.3. A distance of 100m for facilities:

a. Producing fibro-cement and flagstones

b. Producing artificial stones and products from concrete.

c. Casting stones.

d. Producing products from ceramics and fireproof products.

e. Producing glass.

f. Producing building materials using scrap from thermo-electric power plants.

g. Producing products from porcelain.

h. Producing plaster products.

i. Producing products from clay.

j. Producing stones using non-explosive methods and processing natural stones.

4.6. Treating timber and forest products

4.6.1. A distance of 1,000m for facilities:

- a. Producing charcoal not using the pyrolytic method.

4.6.2. A distance of 500m for facilities:

a. Seasoning timber.

a. Producing charcoal by pyrolysis.

4.6.3. A distance of 100m for facilities:

a. Producing wood fiber.

b. Cutting wood; producing plywood and wooden furniture.

c. Building wooden ships and boats.

d. Producing materials from sedge, grass, straw, laminate.

e. Producing products from wood fiber (shavings laminate, wood fiber laminate, wood fiber cement laminate).

f. Producing sedge cloth.

g. Producing wooden furniture, coffins, floor timber.

h. Building wooden ships and boars.

4.7. Textile and garment

4.7.1. A distance of 500m for facilities:

Producing textile and thread using chemicals to treat, bleach and dye.

4.7.2. A distance of 100m for facilities:

- Producing textile and thread without dyeing, producing garment.

4.8. Cellulose and paper

4.8.1. A distance of 1,000m for facilities:

- Producing cellulose by sulphide acid, bisulphide acid and monosulphid acid methods that burn sulphur.

4.8.2. A distance of 500m for facilities:

- Producing fenylaldehyt cloth, paper coils and laminates with production over 100 ton/year.

4.8.3. A distance of 100m for facilities:

a. Producing fenylaldehyt cloth, paper coils and laminates with production under 100 ton/year.

b. Producing various kinds of paper and cardboard, products from wood, bamboo, cellulose without using liquified sulfur gas.

4.9. Tanning leather and products from leather and leatherette

4.9.1. A distance of 500m for facilities:

- Producing leatherette using dusty soluble organic substances.

4.9.2. A distance of 100m for facilities:

a. Producing leatherette using polyvinylchloride and other powders without using dusty soluble organic substances.

b. Tanning cattle

4.10. Food

4.10.1. A distance of 500m for facilities:

a. Being cattle farm with over 1,000 head.

b. Being slaughterhouse that process fish (fat, oil, fin).

c. Being facilities taking fat from sea animals.

d. Being facilities boiling and cleaning food.

e. Being station for rinsing and cleaning the carriages after carrying cattle.

f. Being sugar plants.

g. Being fishery facilities.

4.10.2. A distance of 100m for facilities:

a. Producing albumin.

b. Producing wine.

c. Grinding, producing cattle feed.

d. Producing meat and freezing meat.

e. Treating coffee.

f. Producing vegetable oil.

g. Producing vegetable butter.

h. Being fruit factories.

i. Producing dextrin, sugar, honey.

j. Boiling cheese.

k. Canning fish, processing fish with waste-recycling workshops, fish factory-chains.

l. Producing powder, alcohol and seasoning.

m. Producing cigarettes using yeast.

n. Producing acetone butyl.

o. Producing beer (together with malt and yeast).

p. Producing canned food.

q. Being fruit depots.

r. Producing sugar lumps.

s. Producing noodles.

t. Producing smoked fish.

u. Producing milk and butter (from animals).

v. Producing sausage with production over 3 ton/shift.

w. Producing sweet with production of 20,000 ton/year or above.

x. Producing bread.

y. Processing food.

z. Producing vinegar.

aa.  Freezing food with capacity over 600 ton.

bb. Producing fruit wine.

cc. Producing fruit juice.

dd. Producing Cognac.

ee. Rolling cigarettes, hatched and dried tobacco.

4.11. Hygiene technical constructions and public amenities

4.11.1. A distance of 1,000m for:

a. Yards for storing and classifying rubbish (solids and liquids) and scrap.

b. Ash pile that stinks or discomposing waste pile.

4.11.2. A distance of 500m for:

a. Rubbish recycling and burning plants.

b. Hygienic waste burial yards.

c. Rubbish classification yards.

d. Industrial waste burial yards.

e. Parking yard of means of waste transport.

f. Reservoir for sewage from cities and town, sewage treatment zones.

g. Graveyards

h. Depots for recyclable materials.

4.11.3. A distance of 100m for:

- Temporary depots of untreated waste materials.

III. MANUAL LABOR – STANDARDS OF TASK CLASSIFICATION BY ENERGY CONSUMPTION

1. Scope of regulation: These standards are applicable to dynamic labor tasks (that release apparent energy) These standards do not apply to static labor tasks (that does not release apparent energy).

2. Subjects of application The workers at facilities that employ workers.

3. Definition

The terms in these standards are construed as follows:

- Energy consumption: is the amount of energy being used during the operation or the idle period. Usually represented in watt (W), kilocalorie per minute or per hour (Kcal/minute or Kcal/hour) or Kcal/kg of body weight/minute, or Kcal/minute/m2 of body area.

- Energy consumption by netto: Is the energy consumption while working or resting excluding fundamental metabolism.

- Energy consumption by brutto: Is the energy consumption while working or resting including fundamental metabolism.

4. Standards of classification

Table 1. Classifying tasks by energy consumption

| Class | Brutto energy consumption (Kcal/Kg/minute) |  |
| --- | --- | --- |
|  | Male | Female |
| Light Medium Heavy Very heavy Extremely heavy Maximum | < 0.062 0.062 – 0.080 0.080 – 0.127 0.127 – 0.160 0.160 – 0.200 > 0.20 | < 0.050 0.050 – 0.065 0.065 – 0.095 0.095 – 0.125 0.125 – 0.155 > 0.155 |

IV. MANUAL LABOR – STANDARDS OF TASK CLASSIFICATION BY HEART RATE

1. Scope of regulation: These standards are applicable to the labor tasks (that release apparent energy) in environments of which the temperature does not exceed 320C. These standards do not apply to static labor tasks (that does not release apparent energy).

2. Subjects of application The workers at facilities that employ workers.

3. Definition

The term in these standards is construed as follows:

- Labor heart rate is the heart rate being monitored while the subject has been working at least 3 minutes.

4. Standards of classification

| Class | Heart rate (beat/minute) |
| --- | --- |
| Light Medium Heavy Very heavy Extremely heavy Maximum | < 90 90 - 100 100 - 120 120 - 140 140 - 160 >160 |

Note: The labor heart rate may be extrapolated from the heart rate of the first recovery minute multiplied with 1.14.

V. CARRYING STANDARDS – LIMITED WEIGHT

1. Scope of regulation: These standards specify the maximum carrying weight for each load of a person that have adapted to strenuous manual labor while doing regular or irregular carrying jobs.

2. Subjects of application: the workers at facilities employing workers.

3. Limit values:

| Norm | Limit (kg) |  |
| --- | --- | --- |
|  | Male | Female |
| Regular carrying jobs Irregular carrying jobs | 40 20 | 30 15 |

VI. LIGHTING STANDARDS

1. Scope of regulation: the requirements for lighting hygiene at workplaces in offices and workshops.

2. Subjects of application: the facilities that employ workers. These standards are not applicable to outdoor workplaces.

3. Cited standards

The values specified in these standards are recommendations in ISO 8995-1998 and equivalent to TCVN 3743 – 83.

4. Acceptable values

The minimum light intensity for the works is prescribed in Table 1. The maximum value must not exceed 5,000 lux for filament bulbs and 10,000 lux for fluorescent lamps.

Table 1: Light intensity

| Kind of interior/work | Class of work | Light intensity (lux) |  |
| --- | --- | --- | --- |
|  |  | Fluorescent lamp | Incandescent lamps * |
| Indoor shared areas |  |  |  |
| Ventilation area, corridor | D - E | 50 | 30 |
| Staircase, elevator | C - D | 100 | 50 |
| Locker room, restroom | C - D | 100 | 50 |
| Warehouse | D - E | 100 | 50 |
| Assembly workshops |  |  |  |
| Manual tasks, heavy-duty machine assembly | C - D | 200 | 100 |
| Medium tasks, car assembly | B - C | 300 | 150 |
| Precision works, electronics assembly | A - B | 500 | 250 |
| Precision works, tool assembly | A - B | 1,000 | 500 |
| Chemicals |  |  |  |
| Automated processes | D - E | 50 | 30 |
| Uncrowded production area | C - D | 100 | 50 |
| Shared interior | C - D | 200 | 100 |
| Laboratory | C - D | 300 | 200 |
| Medicine preparation | C - D | 300 | 200 |
| OTK | A - B | 500 | 250 |
| Colorimetry | A - B | 750 | 400 |
| Producing rubber pad | A - B | 300 | 150 |
| Garment industry |  |  |  |
| Sewing | A - B | 500 | 250 |
| OTK | A - B | 750 | 375 |
| Ironing | A - B | 300 | 150 |
| Electricity industry |  |  |  |
| Cable production | B - C | 200 | 100 |
| Telephone network installation | A - B | 300 | 200 |
| Line installation | A - B | 500 | 250 |
| Radio assembly | A - B | 750 | 400 |
| Extreme precision assembly of electronic components | A - B | 1,000 | 500 |
| Food industry |  |  |  |
| Shared working area | C - D | 200 | 100 |
| Automated processes | D - E | 150 | 75 |
| Manual processing, OTK | A - B | 300 | 200 |
| Casting industry |  |  |  |
| Casting workshop | D - E | 150 | 75 |
| Raw casting, core casting | C - D | 200 | 100 |
| Precision casting, core making, OTK | A - B | 300 | 200 |
| Glass and ceramics industry |  |  |  |
| Furnace workshop | D - E | 100 | 50 |
| Casting, molding, mixing room | C - D | 200 | 100 |
| Finishing, glazing, polishing | B - C | 300 | 150 |
| Coloring, decorating | A - B | 500 | 250 |
| Grinding glass, precision works | A - B | 750 | 400 |
| Iron and steel industry |  |  |  |
| Production area without manual work | D - E | 50 | 30 |
| Production area with occasional manual work | D - E | 100 | 50 |
| Fixed workplace in the factory | D - E | 300 | 150 |
| Supervision place and OTK | A - B | 300 | 200 |
| Leather industry |  |  |  |
| Share working area | B - C | 200 | 100 |
| Molding, cutting, sewing, producing shoes | A - B | 500 | 250 |
| Quality testing, classifying, comparing | A - B | 750 | 400 |
| Machine and machine testing |  |  |  |
| Unfixed works | D - E | 150 | 75 |
| Manual works, non-manual works, welding | C - D | 200 | 100 |
| Non-manual works with automated machines | B - C | 300 | 150 |
| Precision works, working with machines, precise machines, machine testing | A - B | 500 | 250 |
| Extremely precise works, measurement, OTK, complicated details | A - B | 1,000 | 500 |
| Painting and coloring |  |  |  |
| Immersion painting, spraying raw paint | D - E | 200 | 100 |
| Usual painting, spraying and finishing | A - B | 500 | 250 |
| Correcting and comparing color | A - B | 750 | 400 |
| Paper industry |  |  |  |
| Producing paper and cardboard | C - D | 200 | 100 |
| Automated production | D - E | 150 | 75 |
| OTK, classification | A - B | 300 | 150 |
| Printing and bookbinding |  |  |  |
| Printer room | C - D | 300 | 150 |
| Editing and reading room | A - B | 500 | 250 |
| Precise testing, revising, acid carving | A - B | 750 | 375 |
| Color publishing and printing | A - B | 1,000 | 500 |
| Carving steel and copper | A - B | 1500 | 750 |
| Bookbinding | A - B | 300 | 150 |
| Typesetting, embossing | A - B | 500 | 250 |
| Textile industry |  |  |  |
| Ornamenting | D - E | 200 | 100 |
| Spinning thread, coiling, winding, dyeing | C - D | 300 | 150 |
| Spinning small thread, weaving | A - B | 500 | 250 |
| Sewing, OTK | A - B | 750 | 375 |
| Carpentry workshop |  |  |  |
| Sawing area | D - E | 150 | 75 |
| Sitting works, assembly | C - D | 200 | 100 |
| Comparing, selecting wood | B - C | 300 | 150 |
| Finishing, OTK | A -B | 500 | 250 |
| Office |  |  |  |
| Shared rooms | A - B | 300 | 150 |
| Professional planning room | A - B | 500 | 250 |
| Graphic room | A - B | 500 | 250 |
| Conference room | A - B | 300 | 150 |
| Shops |  |  |  |
| General lighting at shops |  |  |  |
| Big shopping malls | B - C | 500 | 250 |
| Small shops | B - C | 300 | 150 |
| Supermarket | B - C | 500 | 250 |
| School |  |  |  |
| General lighting | A - B | 300 | 150 |
| Office | A - B | 300 | 150 |
| Briefing room | A - B | 300 | 150 |
| Display room | A - B | 500 | 250 |
| Laboratory | A - B | 300 | 150 |
| Art display room | A - B | 300 | 150 |
| Hall | C - D | 150 | 75 |
| Hospital |  |  |  |
| Areas |  |  |  |
| General lighting | A - B | 50 | 30 |
| Diagnosis room | A - B | 200 | 100 |
| Reading room | A - B | 150 | 100 |
| Night shift | A - B | 3 |  |
| Diagnosis room: |  |  |  |
| General lighting | A - B | 300 | 150 |
| Localized diagnosis | A - B | 750 | 375 |
| Intensive treatment |  |  |  |
| Bed-head | A - B | 30 | 20 |
| Observation place | A - B | 200 | 100 |
| Workplaces of nurses | A - B | 200 | 100 |
| Surgery room |  |  |  |
| General lighting | A - B | 500 | 250 |
| Spot lighting | A - B | 10,000 | 5,000 |
| Automated examination room |  |  |  |
| General lighting | A - B | 500 | 250 |
| Spot lighting | A - B | 5,000 | 2.500 |
| Pharmaceutical and test room |  |  |  |
| General lighting | A - B | 300 | 150 |
| Spot lighting | A - B | 500 | 250 |
| Consultancy room |  |  |  |
| General lighting | A - B | 300 | 150 |
| Spot lighting | A - B | 500 | 250 |

Notes:

- A: Works that require extreme precision

- B: Works that require high precision

- C: Works that require precision

- D: Works that require mediocre precision

- E: Works that require little precision

* For places that use both fluorescent lamps and incandescent lamps, the incandescent lamp intensity shall prevail

VII. MICROCLIMATE STANDARDS

1. Scope of regulation:

These standards specify the temperature, humidity, air speed, heat radiation intensity.

2. Subjects of application: all facilities that employ workers.

3. Cited standards

The value specified in these standards are equivalent to TCVN 5508 - 1991

4. Acceptable values

Table 1: Requirements of temperature, humidity, air speed, heat radiation intensity.

| Time (season) | Work | Air temperature(0C) |  | Air humidity (%) | Air speed (m/s) | Heat radiation intensity (W/m2) |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Max | Min |  |  |  |
| Cold season | Light Medium Heavy |  | 20 18 16 | 80 or under | 0.2 0.4 0.5 | 35 when more than 50% of the human body surface is exposed 70 when more than 25% of the human body surface is exposed |
| Hot season | Light Medium Heavy | 34 32 30 |  | 80 or under | 1.5 | 100 when less than 25% of the human body surface is exposed |

For each measurement:

The temperature must not exceed 320C. The production area must not be hotter than 370C.

The temperature difference between the production area and outdoors is from 30C to 50C.

The relative humidity: 75 - 85%.

The wind speed must not exceed 2m/s.

The heat radiation intensity: 1 cal/cm2/minute.

Table 2: Acceptable limits by Yaglou thermal index

| Kind of work | Light | Medium | Heavy |
| --- | --- | --- | --- |
| Continuous work | 30.0 | 26.7 | 25.0 |
| 50% working, 50% at rest | 31.4 | 29.4 | 27.9 |
| 25% working, 75% at rest | 33.2 | 31.4 | 30.0 |

VIII. STANDARDS OF SILICON DUST

1. Scope of regulation:

These standards specify the limited concentration of the dust that contains silicon dioxide (SiO2).

2. Subjects of application: the facilities that employ workers.

3. Cited standards

The value specified in these standards are equivalent to TCVN 5509 - 1991

4. Limit values:

4.1. The maximum acceptable concentration of dust by particle

Table 1: The maximum acceptable concentration of dust by particle

| Group of dust | Silicon content (%) | Overall dust concentration (particle/cm3) |  | Respiratory dust concentration (particle/cm3) |  |
| --- | --- | --- | --- | --- | --- |
|  |  | By shift | By time | By shift | By time |
| 1 | From over 50 to 100 | 200 | 600 | 100 | 300 |
| 2 | From over 20 to 50 | 500 | 1,000 | 250 | 500 |
| 3 | From over 5 to 20 | 1,000 | 2,000 | 500 | 1,000 |
| 4 | From 5 and fewer | 1,500 | 3,000 | 800 | 1,500 |

4.2. The maximum acceptable concentration of dust by weight

Table 2: The maximum acceptable concentration of dust by weight

| Group of dust | Silicon content (%) | Overall dust concentration (mg/m3) |  | Respiratory dust concentration (mg/m3) |  |
| --- | --- | --- | --- | --- | --- |
|  |  | By shift | By time | By shift | By time |
| 1 | 100 | 0.3 | 0.5 | 0.1 | 0.3 |
| 2 | From over 50 to under 100 | 1,0 | 2.0 | 0.5 | 1.0 |
| 3 | From over 20 to 50 | 2.0 | 4.0 | 1.0 | 2.0 |
| 4 | From 20 and fewer | 3.0 | 6.0 | 2.0 | 4.0 |

IX. STANDARDS OF NON-SILICON DUST

1. Scope of regulation:

These standards specify the limited concentration of the dust without silicon dioxide (SiO2).

2. Subjects of application: the facilities that employ workers.

3. Limit values:

Table 1: The maximum acceptable concentration of non-silicon dust

| Kind | Substance | Overall dust concentration (mg/m3) | Overall dust concentration (mg/m3) |
| --- | --- | --- | --- |
| 1 | Activated carbon, aluminum, bentonite, diatomite, graphite, kaolin, pyrite, talcum powder | 2 | 1 |
| 2 | Bakelite, coal, ferric oxide, zinc oxide, titanium dioxide, silicate, apatite, beryl, phosphatide, limestone, pearlite, marble, portland cement | 4 | 2 |
| 3 | Dust of herb, animal: tea, tobacco, wood dust, cereal dust | 6 | 3 |
| 4 | Organic and inorganic dust not belonging to kind 1, 2, 3 | 8 | 4 |

X. STANDARDS OF COTTON DUST

1. Scope of regulation:

These standards specify the limited concentration of dust of cotton and artificial cotton.

2. Subjects of application: the facilities that employ workers.

3. Limit values:

The maximum acceptable concentration of cotton dust (sampling for 8 hours): 1 mg/m3

XI. STANDARDS OF ASBESTOS DUST

1. Scope of regulation:

These standards specify the acceptable values of vocational exposures to every kind of asbestos dust belonging to the Serpentine (Chrysotile) group in the air of the production area.

2. Subjects of application: the facilities that workers.

3. Limit values:

Table 1: The acceptable values of vocational exposures to asbestos dust

| No. | Substance | In 8 hours (fiber/ml) | In 1 hour (fiber/ml) |
| --- | --- | --- | --- |
| 1 | Serpentine (Chrysotile) | 0.1 | 0.5 |
| 2 | Amphibole | 0 | 0 |

XII. STANDARDS OF NOISE

1. Scope of regulation:

These standards specify the acceptable noise levels at workplaces in workshops, factories and agencies affected by the noise.

2. Subjects of application: Every facility that employs workers.

3. Cited standards

The acceptable values specified in these standards are equivalent to TCVN 3985 - 1999

4. Acceptable levels

4.1. The continuous noise level equivalent to Leq dBA at workplaces must not exceed 85 dBA in 8 hours.

4.2. If the time of exposure to the noise reduces by 50%, the acceptable noise level may increases 5 more dB.

For 4 hours of exposure, 5 dB increased, the acceptable level is 90 dBA

2 hours                                                    95 dBA

1 hour                                                    100 dBA

30 minutes                                              105 dBA

15 minutes                                              110 dBA

< 15 minutes                                            115 dBA

The maximum loudness is 115 dBA.

Only exposure to noise under 80 dBA is acceptable for the remaining time of the working day .

4.3. The acceptable noise pressure level for noise under 5 dB compared to the values specified in section 4.1, 4.2.

4.4. In order to achieve the productivity at various working positions, the noise pressure level at such places must not exceed the values in the below table.

Table 1: The noise pressure level at working positions

| Work positions | Limit of noise level or the equivalent (dBA) | Limit of noise level (dB) of the corresponding octave (Hz) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 63 | 125 | 250 | 500 | 1,000 | 2,000 | 4,000 | 8,000 |
| 1. Working areas of workers, places with workers in workshops and factories | 85 | 99 | 92 | 86 | 83 | 80 | 78 | 76 | 74 |
| 2. Monitoring and remote control rooms without telephone, laboratories, computer rooms with noisy equipment. | 80 | 94 | 87 | 82 | 78 | 75 | 73 | 71 | 70 |
| 3. Monitoring and remote control rooms with telephone, coordination room, precision assembly room, typing room.. | 70 | 87 | 79 | 72 | 68 | 65 | 63 | 61 | 59 |
| 4. Functional, administrative, accounting, planning, statistics rooms. | 65 | 83 | 74 | 68 | 63 | 60 | 57 | 55 | 54 |
| 5. Mental working, designing, researching, statistics, programming, figure processing rooms and theoretic laboratory | 55 | 75 | 66 | 59 | 54 | 50 | 47 | 45 | 43 |

XIII. STANDARDS OF VIBRATION

1. Scope of regulation:

These standards specify the acceptable vibration levels of chairs, working floors, control devices and tool handles that produces vibration affecting the workers during the production.

2. Subjects of application: Every facility that employ workers.

3. Cited standards

These standards are equivalent to TCVN 5127 - 90

4. Acceptable rate

The vibration levels at the working places must not exceed the values specified in Table 1, 2, 3.

Table 1: Vibration of working floors and chairs

| Frequency band (Hz) | Acceptable vibration velocity (cm/s) |  |
| --- | --- | --- |
|  | Vertical vibration | Horizontal vibration |
| 1 (0.88 – 1.4) | 12.6 | 5.0 |
| 2 (1.4 – 2.8) | 7.1 | 3.5 |
| 4 (2.8 – 5.6) | 2.5 | 3.2 |
| 8 (5.6 – 11.2) | 1.3 | 3.2 |
| 16 (11.2 – 22.4) | 1.1 | 3.2 |
| 31.5 (22.4 - 45) | 1.1 | 3.2 |
| 63 (45 - 90) | 1.1 | 3.2 |
| 125 (90 - 180) | 1.1 | 3.2 |
| 250 (180 - 355) | 1.1 | 3.2 |

Table 2: Vibration of control devices

| Frequency band (Hz) | Acceptable vibration velocity (cm/s) |  |
| --- | --- | --- |
|  | Vertical vibration | Horizontal vibration |
| 16 (11.2 – 22.4) | 4.0 | 4.0 |
| 31.5 (22.4 - 45) | 2.8 | 2.8 |
| 63 (45 - 90) | 2.0 | 2.0 |
| 125 (90 - 180) | 1.4 | 1.4 |
| 250 (180 - 355) | 1.0 | 1.0 |

Table 3: Vibration of the tool handles

| Frequency band (Hz) | Acceptable vibration velocity (cm/s) | Correction coefficient k0* |
| --- | --- | --- |
| 8 (5.6 – 11.2) | 2.8 | 0.5 |
| 16 (11.2 – 22.4) | 1.4 | 1 |
| 31.5 (22.4 - 45) | 1.4 | 1 |
| 63 (45 - 90) | 1.4 | 1 |
| 125 (90 - 180) | 1.4 | 1 |
| 250 (180 - 355) | 1.4 | 1 |
| 500 (355 - 700) | 1.4 | 1 |
| 1,000 (700 - 1400) | 1.4 | 1 |

* The correction coefficient k0  is used for calculating the corrective vibration velocity VhD (or total vibration velocity)

The acceptable corrective vibration velocity must not exceed 4 cm/s in 8 hours

The acceptable VhD by time:

8 hours – 4.0 cm/s               4 hours – 5.6 cm/s

7 hours – 4.2 cm/s               3 hours – 6.5 cm/s

6 hours – 4.6 cm/s               2 hours – 8.0 cm/s

5 hours – 5.0 cm/s               1 hours – 11.3 cm/s

< 0.5 hours under 16 cm/s

XIV. STANDARDS OF STATIC MAGNETIC FIELD - MAGNETIC FLUX DENSITY

1. Scope of regulation:

These standards specify the acceptable levels of magnetic flux density of static magnetic field in working environments affected by the static magnetic field.

2. Subjects of application: the facilities that employ workers.

3. Definition

The terms in these standards are construed as follows:

- Medical equipment: is the medical equipment aiding the physiological functions such as pacing systems.

4. Acceptable levels

Table 1: Acceptable levels of magnetic flux density of static magnetic field.

| Subjects of application | 8 hours of exposure | Maximum limit |
| --- | --- | --- |
| Entire body | 60 mT (600G) | 2 T (2.104G) |
| Limbs | 600 mT (6000G) | 5 T (5.104G) |
| Attached medical equipment | - | 0.5 mT (5G) |

XV. STANDARDS OF LOW-FREQUENCY MAGNETIC FIELD - MAGNETIC FLUX DENSITY

1. Scope of regulation:

These standards specify the acceptable levels of magnetic flux density of low-frequency magnetic field at work areas.

2. Subjects of application: the facilities that employ workers.

3. Definition

The terms in these standards are construed as follows:

- Low frequency: are frequencies from 30 KHz and lower.

4. Acceptable levels

Table 1: The acceptable levels of vocational exposures to low-frequency magnetic field

|  | Frequency band |
| --- | --- |
| Acceptable level | Acceptable value  60/f |
| Maximum level | 0.2 mT (2 G) |

- f: the frequency of electric current (in Hz)

XVI. STANDARDS OF INTENSITY OF LOW-FREQUENCY ELECTRIC FIELD AND STATIC ELECTRIC FIELD

1. Scope of regulation:

These standards specify the acceptable levels of magnetic flux density of low frequency magnetic field at working areas.

2. Subjects of application: the facilities that employ workers.

3. Acceptable levels

Table 1: Acceptable levels of intensity of electric field below 30 KHz.

|  | Frequency band |  |  |
| --- | --- | --- | --- |
|  | 0 Hz - 100Hz | 100Hz - 4kHz | 4kHz - 30kHz |
| Maximum value | 25kV/m | (2,5 x 106)/f | 625V/m |

- f: the frequency of electric current (in Hz)

XVII. STANDARDS OF INTENSITY OF ELECTRIC FIELD FROM 30KHz - 300GHz

1. Scope of regulation:

These standards specify the acceptable levels electromagnetic field intensity and the energy density of electromagnetic waves 30kHz-300GHz at working areas.

2. Subjects of application: the facilities that employ workers.

3. Acceptable levels

Table 1a: Acceptable levels of intensity of electromagnetic field from 30KHz-300MHz.

| Frequency | Electromagnetic field intensity (E) (V/m) | Magnetic field intensity (H) (A/m) | Average value of E, H over a period (second) |
| --- | --- | --- | --- |
| 30kHz – 1.5MHz | 50 | 5 | 30 |
| 1.5MHz - 3MHz | 50 | 5 | 30 |
| 3MHz - 30MHz | 20 | 0.5 | 30 |
| 30MHz - 50MHz | 10 | 0.3 | 30 |
| 50MHz - 300MHz | 5 | 0.163 | 30 |

Table 1: Acceptable values of energy density of radiation from 300MHz - 300GHz.

| Frequency | Energy density (W/cm2) | Acceptable exposure duration in 1 day | Notes |
| --- | --- | --- | --- |
| 300MHz - 300GHz | < 10 | 1 day |  |
|  | 10 - 100 | < 2 hours | The energy density must not exceed 10 W/cm2 for the rest. |
|  | 100 - 1,000 | < 20 minutes |  |

Table 2: Acceptable values of contacting current and inductive current.

| Maximum current (mA) |  |  |  |
| --- | --- | --- | --- |
| Frequency | Through 2 feet | Through each foot | Contact |
| 30kHz - 100kHz | 2000f | 1,000f | 1,000f |
| 100kHz - 100MHz | 200 | 100 | 100 |

- f: the frequency of high-frequency electric current (in Hz)

XVIII. ULTRAVIOLET RADIATION – ACCEPTABLE LEVELS

1. Scope of regulation: These standards specify the acceptable values of ultraviolet radiation within the spectrum from 180nm - 400nm (from arc, electric vapor discharge, fluorescence and intensive light sources, solar radiation). Ultraviolet laser is not regulated.

2. Subjects of application: the facilities that employ workers.

3. Definition

The terms in these standards are construed as follows:

- Near-ultraviolet spectrum: are light waves of which the wavelengths range from 315nm - 400nm.

4. Acceptable levels

- The acceptable values of exposure to ultraviolet radiation that damage skin or eyes where the radiation values are known and the exposure durations are controlled:

4.1. Unprotected bare eye exposures to near-ultraviolet spectrum:

a. For duration < 103 seconds, the radiation exposure must not exceed 1,0 J/cm2.

b. For duration ≥103 seconds, the total radiation energy must not exceed 1.0 mW/cm2.

4.2. The exposure of unprotected skin or eyes to ultraviolet radiation must not exceed the values specified in Table 1 in 8 hours

Table 1: Acceptable levels of ultraviolet radiation and spectral weighting function in 8 hours.

| Wavelength (nm) | Acceptable levels (mJ/cm2) | Spectrum intensity coefficient (S) |
| --- | --- | --- |
| 180 | 250 | 0.012 |
| 190 | 160 | 0.019 |
| 200 | 100 | 0.030 |
| 205 | 59 | 0.051 |
| 210 | 40 | 0.075 |
| 215 | 32 | 0.095 |
| 220 | 25 | 0.120 |
| 225 | 20 | 0.150 |
| 230 | 16 | 0.190 |
| 235 | 13 | 0.240 |
| 240 | 10 | 0.300 |
| 245 | 8.3 | 0.360 |
| 250 | 7.0 | 0.430 |
| 254 | 6.0 | 0.500 |
| 255 | 5.8 | 0.520 |
| 260 | 4.6 | 0.650 |
| 265 | 3.7 | 0.810 |
| 270 | 3.0 | 0.1 |
| 275 | 3.1 | 0.960 |
| 280 | 3.4 | 0.880 |
| 285 | 3.9 | 0.770 |
| 290 | 4.7 | 0.640 |
| 295 | 5.6 | 0.540 |
| 297 | 6.5 | 0.460 |
| 300 | 10 | 0.300 |
| 303 | 25 | 0.120 |
| 305 | 50 | 0.060 |
| 308 | 120 | 0.026 |
| 310 | 200 | 0.015 |
| 313 | 500 | 0.006 |
| 315 | 1.0 x 103 | 0.003 |
| 316 | 1.3 x 103 | 0.0024 |
| 317 | 1.5 x 103 | 0.0020 |
| 318 | 1.9 x 103 | 0.0016 |
| 319 | 2.5 x 103 | 0.0012 |
| 320 | 2.9 x 103 | 0.0010 |
| 322 | 4.5 x 103 | 0.00067 |
| 323 | 5.6 x 103 | 0.00054 |
| 325 | 6.0 x 103 | 0.00050 |
| 328 | 6.8 x 103 | 0.00044 |
| 330 | 7.3 x 103 | 0.00041 |
| 333 | 8.1 x 103 | 0.00037 |
| 335 | 8.8 x 103 | 0.00034 |
| 340 | 1.1 x 104 | 0.00028 |
| 345 | 1.3 x 104 | 0.00024 |
| 350 | 1.5 x 104 | 0.00020 |
| 355 | 1.9 x 104 | 0.00016 |
| 360 | 2.3 x 104 | 0.00013 |
| 365 | 2.7 x 104 | 0.00011 |
| 370 | 3.2 x 104 | 0.000093 |
| 375 | 3.9 x 104 | 0.000077 |
| 380 | 4.7 x 104 | 0.000064 |
| 385 | 5.7 x 104 | 0.000053 |
| 390 | 6.8 x 104 | 0.000044 |
| 395 | 8.3 x 104 | 0.000036 |
| 400 | 1.0 x 105 | 0.000030 |

Table 2: Acceptable levels of ultraviolet radiation.

| Exposure duration/day | Effective radiation Eeff (W/cm2) |
| --- | --- |
| 8 hours | 0.1 |
| 4 hours | 0.2 |
| 2 hours | 0.4 |
| 1 hour | 0.8 |
| 30 minutes | 1.7 |
| 15 minutes | 3.3 |
| 10 minutes | 3.3 |
| 5 minutes | 10 |
| 1 minute | 50 |
| 30 seconds | 100 |
| 10 seconds | 300 |
| 1 second | 3,000 |
| 0.5 second | 6,000 |
| 0.1 second | 30,000 |

XIX. STANDARDS OF RADIOACTIVITY

1. Scope of regulation:

These standards specify the acceptable values of doses and levels of radioactive substances and radioactive rays at workplaces.

2. Subjects of application: These standards are applicable to people that directly or indirectly work with ionizing radiation. The general residents are not regulated.

3. Definition

The terms in these standards are construed as follows:

- Ionizing radiation, as known as radioactivity, are all kinds of radiations (electromagnetic and particle radiation) that creates ions when interacting with the environment.

- Radiation bases: are places that use radiation sources such as:

+ X-ray devices, -ray emitters

+ Sources of closed radiation such as: Radium 226, cobalt, Strontium 90.

+ Sources of open radiation such as: I-131, P-32, U-238, Th-232.

- External radiation: radiation from a source outside the body.

- Internal radiation: radiation from a source inside the body.

- Equivalent dose: is the equivalent dose for a period of time (Rem/hour). Rem: Roentgent equivalent in man.

- Control zone: is the contiguous zones around the radiation bases or the radioactive gas discharge pipe

- Supervision zone: is the area outside the control zone that might be affected by the gaseous, liquid or solid radioactive substances.

4. Cited standards

- These standards are equivalent to TCVN 4397 - 87

5. Acceptable doses

The equivalent dose at working positions of the radiation bases must not exceed the values specified in Table 1.

Table 1: Acceptable equivalent dose

| Radiated subjects | Workplace | P (mrem/h) with t  40h/week |
| --- | --- | --- |
| Subject A | - Regular workplaces - Workplaces under 20h/week | 1.2 2.4 |
| Subject B | - In other working rooms within the control zone - In supervision zones | 0.12 0.03 |

Notes: Subject A: Radiation worker

Subject B: Adjacent people

5.2. The limited doses in a year (for both internal and external radiation) of the radiated subjects and the vital organs are specified in Table 2:

Table 2: Limited dose in a year

| Human subject | Limited dose for vital organs (rem/year) |  |  |
| --- | --- | --- | --- |
|  | Group I | Group II | Group III |
| A | 5 | 15 | 30 |
| B | 0.5 | 1.5 | 3 |

Notes:

- Group I: whole-body, gonads, bone marrow.

- Group II: Organs outside Group I and III

- Group III: Skin, tissue, bones, hands, legs, feet, ankles

5.3. The limited density of radioactive substances in the air or workplaces are specified in Table 3. That of the radioactive compounds with unknown compositions are specified in Table 4.

5.4. The radioactive contamination levels of surfaces at workplaces and protective instruments are specified in Table 5.

5.5. The total accumulative doses of Subject A at any age over 18 are calculated by the formula:

D  5 (N - 18)

- D: Dose (in Rem).

- N: Age (in year).

If necessary, the accumulative dose may reach 12 rem/year, but then must be offset in 5 years so that the total dose would not exceed D.

Table 3: The limited air density of nuclides of which the compositions are totally or partly unknown (Ci/l)

| The composition of radioactive nuclide mixtures that contaminate through the respiratory tract | Subject A | Subject B |
| --- | --- | --- |
| Unknown composition | 4 x 10-16 | 1 x 10-17 |
| The composition does not contain Cm-248 | 8 x 10-16 | 3 x 10-17 |
| The composition does not contain: PA-231, Pu 239, Pu-240. Pu 242, Cm-248, Cf-249, Cf-251 | 2 x 10-15 | 5 x 10-17 |
| The composition does not contain: Ac-227, Th-230. Pa-231, Pu238, Pu-239, Pu-240. Pu-242, Pu-244, Cm-248, Cf-249, Cf-251 | 4 x 10-15 | 1 x 10-16 |
| The composition does not contain any alpha radiation and Ac-227 | 2 x 10-14 | 8 x 10-16 |
| The composition does not contain any alpha radiation and Pb-210. Ac-227, Ra-228, Pu-241 | 2 x 10-13 | 8 x 10-15 |
| The composition does not contain any alpha radiation and Sr-90. I-192, Pb-210. Ac-227, Ra-228, Pa-230. Pu-241, Bk-249 | 2 x 10-16` | 8 x 10-13 |

Table 4: The limited density of radioactive substances in the working air

| No. | Radioactive nuclide | Form in compounds | Limited density in the working air Ci/l |  | No. | Radioactive nuclide | Form in compounds | Limited density in the working air Ci/l |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Subject A | Subject B |  |  |  | Subject A | Subject B |
| 1 | H-3(T) | Insoluble Soluble | 2.0x10-6 4.8x10-9 | 6.6x10-8 1.6x10-10 | 31 | Co-57 | Soluble Insoluble | 1.6x10-11 | 5.5x10-12 |
| 2 | C-14 | Soluble | 3.5x10-9 | 1.2x10-10 | 32 | Co-58 | Soluble Insoluble | 5.6x10-11 | 1.9x10-12 |
| 3 | F-18 | Soluble Insoluble | 2.6x10-9 | 8.7x10-11 | 33 | Co-60 | Soluble Insoluble | 8.8x10-12 | 3.0x10-13 |
| 4 | Na-22 | Soluble Insoluble | 8.4 x10-12 | 2.9x10-13 | 34 | Ni-63 | Soluble Insoluble | 6.4x10-11 | 2.2x10-12 |
| 5 | Na-24 | Soluble Insoluble | 1.4x10-10 | 4.9x10-12 | 35 | Cu-64 | Soluble Insoluble | 1.0x10-9 | 3.6x10-11 |
| 6 | P-32 | Soluble Insoluble | 7.2x10-11 | 2.4x10-12 | 36 | Zn-65 | Soluble Insoluble | 6.0x10-11 | 2.6x10-12 |
| 7 | S-35 | Soluble Insoluble | 3.6x10-11 | 1.2x10-12 | 37 | As-74 | Soluble Insoluble | 1.2x10-10 | 4.2x10-12 |
| 8 | Cl-36 | Soluble Insoluble | 2.3x10-11 | 7.8x10-13 | 38 | Se-75 | Soluble Insoluble | 1.2x10-10 | 4.2x10-12 |
| 9 | K-42 | Soluble Insoluble | 1.1x10-10 | 3.7x10-12 | 39 | Br-82 | Soluble Insoluble | 1.9x10-10 | 6.4x10-12 |
| 10 | Ca-43 | Soluble | 3.2x10-11 | 1.1x10-12 | 40 | Rb-86 | Soluble Insoluble | 6.8x10-11 | 2.3x10-12 |
| 11 | Ca-47 | Insoluble | 1.7x10-10 | 5.8x10-12 | 41 | Sr-89 | Soluble | 2.8x10-11 | 9.4x10-13 |
| 12 | Cr-51 | Soluble Insoluble | 2.2x10-9 | 7.7x10-11 | 42 | Sr-90 | Soluble | 1.2x10-12 | 4.0x10-14 |
| 13 | Mn-52 | Soluble Insoluble | 1.4x10-10 | 4.8x10-12 | 43 | Y-90 | Soluble Insoluble | 1.0x10-10 | 3.5x10-12 |
| 14 | Mn-54 | Soluble Insoluble | 3.6x10-11 | 1.2x10-12 | 44 | Zr-93 | Soluble Insoluble | 1.3x10-10 | 4.4x10-12 |
| 15 | Fe-55 | Soluble Insoluble | 8.4x10-10 | 2.9x10-11 | 45 | Tc-99m | Soluble Insoluble | 1.4x10-9 | 4.8x10-10 |
| 16 | Fe-59 | Soluble Insoluble | 5.2x10-11 | 1.8x10-12 | 46 | Tc-99 | Soluble Insoluble | 6.0x10-11 | 2.1x10-12 |
| 17 | Mo-99 | Soluble Insoluble | 2.0x10-10 | 6.9x10-12 | 47 | Au-198 | Soluble Insoluble | 2.4x10-10 | 8.0x10-12 |
| 18 | In-113m | Soluble Insoluble | 6.8x10-9 | 2.3x10-10 | 48 | Hg-197 | Soluble Insoluble | 1.2x10-9 | 4.0x10-11 |
| 19 | Sb-124 | Soluble Insoluble | 1.9x10-11 | 6.6x10-13 | 49 | Hg-203 | Soluble Insoluble | 7.2x10-11 | 2.5x10-12 |
| 20 | I-125 | Soluble | 4.8x10-12 | 1.6x10-13 | 50 | TI-201 | Soluble Insoluble | 8.8x10-10 | 3.0x10-11 |
| 21 | I-126 | Soluble | 3.6x10-12 | 1.2x10-13 | 51 | Pb-210 | Soluble Insoluble | 6.0x10-14 | 2.0x10-13 |
| 22 | I-129 | Soluble | 8.0x10-13 | 2.7x10-14 | 52 | Po-21 | Soluble Insoluble | 9.3x10-14 | 3.1x10-15 |
| 23 | I-131 | Soluble | 4.2x10-12 | 1.5x10-13 | 53 | Ra-226 | Soluble Insoluble | 2.5x10-14 | 8.5x10-18 |
| 24 | Cs-131 | Soluble Insoluble | 1.0x10-8 | 3.6x10-10 | 54 | Th-232 | Soluble Insoluble | 1.0x10-15 | 2.5x10-14 |
| 25 | Cs-134m | Soluble Insoluble | 6.0x10-9 | 2.0x10-10 | 55 | U-235 7.1x 10-8năm | Soluble Insoluble | 6.0x10-14 |  |
| 26 | Cs-134 | Soluble Insoluble | 1.3x10-11 | 4.4x10-14 | 56 | U-238 | Soluble Insoluble | 6.3x10-14 | 2.2x10-15 |
| 27 | Cs-137 | Soluble Insoluble | 1.4x10-14 | 4.9x10-13 | 57 | Am-241 | Soluble Insoluble | 3.0x10-15 | 1.0x10-16 |
| 28 | Ba-131 | Soluble Insoluble | 3.5x10-10 | 1.2x10-11 | 58 | Cm-244 | Soluble Insoluble | 46x10-15 | 1.5x10-16 |
| 29 | La-140 | Soluble Insoluble | 1.2x10-10 | 4x10-12 | 59 | Cf-252 | Soluble Insoluble | 3.2x10-15 | 1.1x10-16 |
| 30 | Ir-192 | Soluble Insoluble | 2.6x10-11 | 8.7x10-13 |  |  |  |  |  |

Notes:  Other specifications of the radioactive nuclides in this Table can be found in "Safety Norm of ionizing radiation” TCVN 4397-87

Table 5: Contamination levels of surfaces (particle/cm2/minute)(1)

| Contaminated subject | Nuclide emitting alpha particle |  | Nuclide emitting beta particle (4) |
| --- | --- | --- | --- |
|  | Special nucleus(2) | Other nuclei |  |
| Skin, towel, internal clothes, inner side of the front side of personal safety instruments. | 1 | 1 | 100 |
| Primary safety outfit, inner side of additional safety instruments | 5 | 20 | 800 |
| Surface of rooms with regular workers, outer side of additional safety instrument in these rooms. | 5 | 20 | 2,000 |
| Surface of machinery rooms without regular workers, outer side of additional safety instrument in these rooms. | 50 | 200 | 8,000 |
| Means of transport, outer side of containers and wrap of radioactive substances in the control zones(3). | 10 | 10 | 100 |

Notes:

(1) For surfaces of working rooms, equipment, means of transport, containers, wrap, the contamination level is determined using dry cleaning method according to the non-sticky contamination amount (cleanable). For other cases, the contamination levels are determined by the total contamination level (non-sticky and sticky)

(2) Special nuclides are nuclides that emit alpha particles with acceptable density in the working air being 1.10-14 Curi/liter.

(3) The radioactive contamination on the outer side of the radioactive substance container and means of transport are not allowed outside the control zone.

(4) For Sr-90. Sr-90 + Y-90, the acceptable contamination level is 5 times lower. The tritium contamination is not regulated because it is controlled by the content in the air and in the body.

XX. X-RAY RADIATION – ACCEPTABLE LEVELS

1. Scope of regulation:

These standards specify the requirements for radiation safety of medical X-ray facilities.

2. Subjects of application: medical X-ray facilities.

3. Definition

The terms in these standards are construed as follows:

- Medical X-ray facilities are medical facilities using X-ray devices for medical examination and treatment.

4. Cited standards

These standards are equivalent to TCVN 6561-1999

5. Acceptable levels

5.1. Limited doses

Table 1: Acceptable doses in a year

| Kind of dose and subjects of application | Radiation worker | Apprentice from 16-18 years old | Other people |
| --- | --- | --- | --- |
| Systemic effective dose | 20mSv | 6mSv | 1mSv |
| Equivalent dose for crystalline lens | 150mSv | 50mSv | 15mSv |
| Equivalent dose for limbs or skin | 500mSv | 150mSv | 50mSv |
| Lounge and waiting room |  |  | 1mSv |

Notes: - The doses when working with X-ray do not include natural background radiation.

- Doses for special cases are specified in the Annex

Table 2: Acceptable instantaneous doses in X-ray rooms

| Location | Dose (Sv/h) |
| --- | --- |
| - Directly radiated workers | 10.0 |
| - Film development room | 0.50 |
| - Patient waiting room or lounge | 0.50 |
| - Working rooms and workplaces of employees | 0.50 |
| - The outer side X-ray machine | 0.50 |

5.2.  Limited doses in special cases

5.2.1. Effective doses for radiation worker: 20mSv, averagely sampled in 5 consecutive working years. The dose may reach 50mSv in a single year but the average dose in 5 years must not exceed 20mSv/year.

The effective dose for radiation workers is 20mSv/year being averagely sampled in 10 consecutive working years and the dose in any single year does not exceed 50mSv.

When the accumulative effective dose of a radiation worker reaches 100mSv, it must be reconsidered.  If his/her health is still normal without manifestation of radioactive impacts, the blood formula is still unchanged etc., the work may continue.

5.2.2. Effective doses for other people: The dose may reach 5 mSv in a single year but the average dose in 5 consecutive years must not exceed 1 mSv/year The layout, sizes and radiation protection methods are specified in the Annex.

5.3. Location of a X-ray facility

The X-ray facility must be isolated from paediatrics, obstetrics, crowded areas etc,  especially the tenements.

5.4. Layout  of a X-ray facility

Each X-ray facility must contain at least the following rooms:

- The patient waiting room or lounge,

- The X-ray machine room,

- The film development room,

- The working room or place of radiation workers.

5.4.1. The Patient waiting room or lounge:

- The patient waiting room (or lounge) must be separated from the X-ray room. The limited dose in this room must not exceed 1mSv/year.

5.4.2. The X-ray machine room must satisfy the following requirements:

- Convinient for the installation and operation, safe for the patients to moves. The minimum area is 25 m2, the minimum width is 4.5 m, the minimum height is 3m for an ordinary X-ray machine.

- The breast, teeth X-ray machines and CT scanners must comply with the standardized size in Table 3.

Table 3: The minimum size of working rooms for medical X-ray machines

| Work | Room area | Minimum side length |
| --- | --- | --- |
| - (CT scanner room) + 2-dimension + 3-dimension | 28 m2 40 m2 | 4 m 4 m |
| - X-ray room for teeth | 12 m2 | 3 m |
| - X-ray room for breast | 18 m2 | 4 m |
| - X-ray machine with contrast medium | 30 m2 | 4.5 m |
| - X-ray machine with signal contrast medium | 36 m2 | 5.5 m |
| - Automated dark room | 7 m2 | 2.5 m |
| - Non-automated dark room | 8 m2 | 2.5 m |

- If the room design for new machines recommended by the producer is smaller than the above measurements, the consent of competent State agencies is compulsory.

- The thickness of the walls, the ceiling, the floor and the doors of the X-ray machine room must be calculated and designed in accordance with specifications of the equipment (voltage, current intensity), operation duration and the outer occupation coefficient of the X-ray room.

- The minimum height of the vents and windows of the X-ray room where people pass by is 2 m from the floor outside the X-ray room.

- The radiation signal light must be put at the eye level outside the door of the X-ray room. The signal light must glow throughout the radiation emission of the machine.

- The X-ray machine installation must ensure that the X-ray beam is not emitted toward the door or places with many people, and the eyes must be protected from the radiation sources. The shield height must be over 2m from the floor, the minimum width is 90cm and the corresponding thickness is 1.5mm of lead.

- For rooms with 2 X-ray machines, only 1 is allowed to operate at a time.

- The control panel is put inside or outside the X-ray room depending on the machine itself. There must be lead glass for observing the patient. The limited dose at the control panel must not exceed 20 mSv/year (excluding natural background radiation).

5.4.3. The film development room (the dark room):

- The dark room must be separated from the X-ray room.

- The dose in the dark room must not affect the film development. The undeveloped film must not be radiated over 1 mSv/year, excluding natural background radiation.

- The dark room door must not be directly radiated.

- The cassette pass box in the X-ray room must be covered with 2 mm lead.

5.4.4. The working room (or place) of radiation workers:

- The working room (or place) of radiation workers must be separated from the X-ray room. The doses in the room must not exceed 1 mSv/year, excluding natural background radiation.

XXI. CHEMICALS – ACCEPTABLE LIMITS IN THE WORKING AIR

1. Scope of regulation

These standards specify the maximum acceptable density of a number of chemicals in the working air.

2. Subjects of application

These standards are applicable to facilities that employ workers (production facilities, trading and service establishments…)

These standards are not applicable to the air in residential areas.

3. Limit values

Table 1: Limit values of chemicals in the air at working areas

| No. | Chemical name | Chemical formula | Average value in 8 hours (mg/m3) (TWA) | Maximum value at a time (mg/m3) (STEL) |
| --- | --- | --- | --- | --- |
| 1 | Acrolein | CH2CHCHO | 0.25 | 0.50 |
| 2 | Acrylic amide | CH2CHCONH2 | 0.03 | 0.2 |
| 3 | Acrylonitrile | CH2CHCN | 0.5 | 2,5 |
| 4 | Allyl acetate | C5H8O3 | - | 2 |
| 5 | Ammonia | NH3 | 17 | 25 |
| 6 | Amyl acetate | CH3COOC5H11 | 200 | 500 |
| 7 | Phthalic anhydride | C8H4O3 | 2 | 3 |
| 8 | Aniline | C6H5NH2 | 4 | 8 |
| 9 | Antimony | Sb | 0.2 | 0.5 |
| 10 | ANTU | C10H7NHC(NH2)S | 0.3 | 1.5 |
| 11 | Arsenic and compounds | As | 0.03 | - |
| 12 | Arsine | AsH3 | 0.05 | 0.1 |
| 13 | Asphalt |  | 5 | 10 |
| 14 | Acetone | (CH3)2CO | 200 | 1,000 |
| 15 | Acetone cyanohydrin | CH3C(OH)CNCH3 | - | 0.9 |
| 16 | Acetonitrile | CH3CN | 50 | 100 |
| 17 | Acetylene | C2H2 | - | 1,000 |
| 18 | 2, 4 - D (Dichloro - phenoxyacetic acid) | Cl2C6H3OCH2COOH | 5 | 10 |
| 19 | 2, 4, 5 - T (Trichloro - phenoxyacetic acid) | C6 H2Cl3OCH2COOH | 5 | 10 |
| 20 | Acetic acid | CH3COOH | 25 | 35 |
| 21 | Boric acid and compounds | H2BO3 | 0.5 | 1 |
| 22 | Hydrochloric acid | HCl | 5 | 7,5 |
| 23 | Formic acid | HCOOH | 9 | 18 |
| 24 | Methacrylic acid | C4H6O2 | 50 | 80 |
| 25 | Nitrous acid | HNO2 | 45 | 90 |
| 26 | Nitric acid | HNO3 | 5 | 10 |
| 27 | Oxalic acid | (COOH)2.2H2O | 1 | 2 |
| 28 | Phosphoric acid | H3PO4 | 1 | 3 |
| 29 | Picric acid | HOC6H2(NO2)3 | 0.1 | 0.2 |
| 30 | Sulfuric acid | H2SO4 | 1 | 2 |
| 31 | Thioglycolic acid | C2H4O2S | 2 | 5 |
| 32 | Trichloroacetic acid | C2HCl3O2 | 2 | 5 |
| 33 | Azinphos methyl | C10H12O3 PS2N3 | 0.02 | 0.06 |
| 34 | Aziridine | H2CNHCH2 | 0.02 | - |
| 35 | Silver | Ag | 0.01 | 0.1 |
| 36 | Silver compounds | như Ag | 0.01 | 0.03 |
| 37 | Barium oxide | BaO2 | 0.6 | 6 |
| 38 | Benomyl | C14H18N4O3 | 5 | 10 |
| 39 | Benzene | C6H6 | 5 | 15 |
| 40 | Benzidine | NH2C6H4C6H4NH2 | 0.008 | - |
| 41 | Benzonitrile | C7H5N | - | 1 |
| 42 | Benzopyrene | C20H12 | 0,0001 | 0,0003 |
| 43 | (o, p) Benzoquinone | C6 H4O2 | 0.4 | 1,0 |
| 44 | Benzotrichloride | C7H5 Cl3 | - | 0.2 |
| 45 | Benzoyl peroxide | C14H10O4 | - | 5 |
| 46 | Benzylchloride | C6H5CH2 Cl | - | 0.5 |
| 47 | Beryllium and compounds | Be | - | 0.001 |
| 48 | Polychlorinated biphenyls | C12H10-xCx | 0.01 | 0.02 |
| 49 | Boron trifluoride | BF3 | 0.8 | 1 |
| 50 | Bromine | Br2 | 0.5 | 1 |
| 51 | Bromoethane | C2H5Br | 500 | 800 |
| 52 | Bromomethane | CH3Br | 20 | 40 |
| 53 | Bromine pentafluoride | BrF5 | 0.5 | 1 |
| 54 | 1,3-Butadiene | CH2CHCHCH2 | 20 | 40 |
| 55 | Butyl acetate | CH3 COO[CH2]3 CH3 | 500 | 700 |
| 56 | Butanols | CH3(CH2)3 OH | 150 | 250 |
| 57 | Octa decanoic acid, cadmium | C36H72O4Cd | 0.04 | 0.1 |
| 58 | Cadmium and compounds | Cd | 0.01 | 0.05 |
| 59 | Carbondioxide | CO2 | 900 | 1800 |
| 60 | Carbon disulfide | CS2 | 15 | 25 |
| 61 | Carbonmonoxide | CO | 20 | 40 |
| 62 | Carbontetrachlorie | CCl4 | 10 | 20 |
| 63 | Carbofuran | C17H15O3N | 0.1 | - |
| 64 | Carbonyl fluoride | COF2 | 5 | 13 |
| 65 | Calcium carbonate | CaCO3 | 10 | - |
| 66 | Calcium chromate | CaCrO4 | 0.05 | - |
| 67 | Calcium hydroxyde | Ca(OH)2 | 5 | - |
| 67 | Calcium oxide | CaO | 2 | 4 |
| 69 | Calcium silicate | CaSiO3 | 10 | - |
| 70 | Calcium sulfate dihydrate | CaSO4.2H2O | 6 | - |
| 71 | Calcium cyanamide | C2CaN2 | 0.5 | 1.0 |
| 72 | Caprolactam (dust) | C6H11NO | 1 | 3 |
| 73 | Caprolactam (fume) | C6H11NO | 20 | - |
| 74 | Captan | C9H8 Cl3NO2S | 5 | - |
| 75 | Carbaryl | C10H7O O CNHCH3 | 1 | 10 |
| 76 | Catechol | C15H14O6 | 20 | 45 |
| 77 | Lead tetraethyl | Pb(C2H5)4 | 0.005 | 0.01 |
| 78 | Lead and compounds | Pb | 0.05 | 0.1 |
| 79 | Chlorine | Cl2 | 1.5 | 3 |
| 80 | Chloroacetaldeh-yde | ClCH2CHO | 3 | - |
| 81 | Chlorine dioxide | ClO2 | 0.3 | 0.6 |
| 82 | Chloroacetophe-none | C6H5COCH2Cl | 0.3 | - |
| 83 | Chlorobenzene | C6H5Cl | 100 | 200 |
| 84 | 1- Chloro - 2,4 -dinitro - benzene | C6H3ClN2O4 | 0.5 | 1 |
| 85 | Chloronitrobenzene | C6H4ClNO2 | 1 | 2 |
| 86 | Chloroprene | CH2CClCHCH2 | 30 | 60 |
| 87 | 1- Chloro 2 - propanone | C3H5ClO | - | 3 |
| 88 | Chloroform | CHCl3 | 10 | 20 |
| 89 | Chloropicrin | CCl3NO2 | 0.7 | 1.4 |
| 90 | 3-Chloropropene | C2H5Cl | 1 | 2 |
| 91 | Chlorotrifluoroethy-lene | C2ClF3 | - | 5 |
| 92 | Cobalt and compounds | Co | 0.05 | 0.1 |
| 93 | Cresol | C7H8O | 5 | 10 |
| 94 | Chromium trioxide | CrO3 | 0.05 | 0.1 |
| 95 | Chromium (III) compounds | Cr+3 | 0.5 | - |
| 96 | Chromium (VI) compounds | Cr+4 | 0.05 | - |
| 97 | Chrom (VI) compound (water soluble) | Cr+6 | 0.01 | - |
| 98 | Crotonaldehyde | CH3CHCHCHO | 5 | 10 |
| 99 | Cumene | C6H5CH(CCH3)2 | 80 | 100 |
| 100 | Mineral (mist) |  | 5 | 10 |
| 101 | Petroleum distillates (naphta) |  | 1600 | - |
| 102 | Turpentine | C10H16 | 300 | 600 |
| 103 | Vegetable oil mist |  | 10 | - |
| 104 | Diamino 4, 4’-diphenyl methane | NH2C6H4C6H4NH2 | - | 0.8 |
| 105 | Dimethyl - 1, 2 - dibromo - 2,2 - dichlorethyl phosphate (Naled) | (CH3O)2POOCHBrCBrCl2 | 3 | 6 |
| 106 | Rubber solvent |  | 1570 | - |
| 107 | Stoddard solvent (White spirit) |  | 525 |  |
| 108 | Soapston | 3MgO.4SiO2.H2O | 3 | - |
| 109 | Soapstone | 3MgO.4SiO2.H2O | 6 | - |
| 110 | Decalin | C10H18 | 100 | 200 |
| 111 | Demeton | C8H19O3PS2 | 0.1 | 0.3 |
| 112 | Diazinon | C12H21N2O3PS | 0.1 | 0.2 |
| 113 | Diborane | B2H6 | 0.1 | 0.2 |
| 114 | 1,2 - Dibromo - 3 chloro - propane | C3H5Br2Cl | 0.01 | - |
| 115 | Dibutyl phthalate | C6H4(CO2C4H9)2 | 2 | 4 |
| 116 | Dichloroacetylene | ClCCCl | 0.4 | 1.2 |
| 117 | Dichlorobenzene | C6H4Cl2 | 20 | 50 |
| 118 | Dichloroethane | CH3CHCl2 | 4 | 8 |
| 119 | 1,1- Dichloroethylene | C2H2Cl2 | 8 | 16 |
| 120 | Dichloroethylene (1,2; Cis; Trans) | C2H2Cl2 | 790 | 1,000 |
| 121 | Dichloromethane | CH2Cl2 | 50 | 100 |
| 122 | 1,2- Dichloropropan | C3H6Cl2 | 50 | 100 |
| 123 | Dichloropropene | C3H4Cl2 | 5 | - |
| 124 | Dichlorostyrene | C8H6Cl2 | 50 | - |
| 125 | Dichlorvos | (CH3O)2PO2CHCCl2 | 1 | 3 |
| 126 | Dicrotophos | C8H16NO5P | 0.25 | - |
| 127 | Dimethylamine | C2H7N | 1 | 2 |
| 128 | Dimethyl formamide | (CH3)2NCHO | 10 | 20 |
| 129 | 1,1 Dimethyl hydrazine | (CH3)2 NNH2 | 0.2 | 0.5 |
| 130 | Dimethyl phenol | C8H10O | - | 2 |
| 131 | Dimethyl sulfate | (CH3)2SO4 | 0.05 | 0.1 |
| 132 | Dimethyl sulfoxide | C2H6OS | 20 | 50 |
| 133 | Dinitrobenzene | C7H6N2O4 | - | 1 |
| 134 | Dinitrotoluene (DNT) | C6 H5CH3(NO2)2 | 1 | 2 |
| 135 | Dioxathion | C12 H26O6P2S4 | 0.2 | - |
| 136 | Diquat Dibromide | C12 H12N2.2Br | 0.5 | 1 |
| 137 | 1,4-Dioxane | OCH2CH2OCH2CH2 | 10 | - |
| 138 | Copper (dust) | Cu | 0.5 | 1 |
| 139 | Copper (fume) | Cu | 0.1 | 0.2 |
| 140 | Copper compounds | Cu | 0.5 | 1 |
| 141 | Endousulfan | C9H6Cl6O3S | 0.1 | 0.3 |
| 142 | 2, 3 - Epoxy 1 - propanol | C3H6O2 | 1 | 5 |
| 143 | EPN (o - ethyl - o - paranitrophenyl - phosphonothioate) | C18H14NO4PS | 0.5 | - |
| 144 | Ethanolamine | NH2C2H4OH | 8 | 15 |
| 145 | Diglycidyl ether | C6H10O3 | 0.5 | - |
| 146 | Chloroethyl ether | C4H8Cl2O | - | 2 |
| 147 | Chloromethyl ether | (CH2Cl)2O | 0.003 | 0.005 |
| 148 | Ethyl ether | C2H5OC2H5 | 1,000 | 1,500 |
| 149 | Isopropyl glycidyl ether | (CH3)2CHOCH(CH3)2 | 200 | 300 |
| 150 | Resorcinol monomethyl Ether | C7H8O2 | - | 5 |
| 151 | Ethylamine | CH3CH2NH2 | 18 | 30 |
| 152 | Ethylene | C2H4 | 1,150 | - |
| 153 | Ethanethiol (Ethylmercaptan) | C2H5SH | 1 | 3 |
| 154 | Ethylene dibromide | BrCH2 CH2Br | 1 | - |
| 155 | Ethylene glycol |  | 10 | 20 |
| 156 | Ethylene glycol | C2H6O2 | 60 | 125 |
| 157 | Ethylene glycol dinitrate | C2H4(O2NO)2 | 0.3 | 0.6 |
| 158 | Ethylene oxide | C2H4O | 1 | 2 |
| 159 | Perchloroethylene | C2Cl4 | 70 | 170 |
| 160 | Ethylidene norbornene | C9H12 | - | 20 |
| 161 | Fensulfothion | C11H17O4PS2 | 0.1 | - |
| 162 | Fenthiol | C10H15O3PS2 | 0.1 | - |
| 163 | Fluorine | F2 | 0.2 | 0.4 |
| 164 | Fluorides |  | 1 | 2 |
| 165 | Formaldehyde | HCHO | 0.5 | 1 |
| 166 | Formamide | HCONH2 | 15 | 30 |
| 167 | Furfural | C4H3OCHO | 10 | 20 |
| 168 | Furfuryl alcohol | C5H6O2 | 20 | 40 |
| 169 | Coal Tar pitch volatiles |  | - | 0.1 |
| 170 | Halothane | C2HBrClF3 | 8 | 24 |
| 171 | Mekuran (mixture of ethylmer cuirc chloride and lindane) |  | 0.005 | - |
| 172 | Heptachlor (iso) | C10H5Cl7 | 0.5 | 1,5 |
| 173 | Heptan | C7H14 | 800 | 1,250 |
| 174 | Hexachlorobenzene | C6Cl6 | 0.5 | 0.9 |
| 175 | Hexachloro 1,3-butadiene | C4Cl6 | - | 0.005 |
| 176 | 1, 2, 3, 4, 5, 6 - hexachloro-cyclohexane | C6H6Cl6 | 0.5 | - |
| 177 | Hexachlorocyclopen-tadiene | C5Cl6 | 0.01 | 0.1 |
| 178 | Hexafluoroacetone | (CF3)2CO | 0.5 | 0.7 |
| 179 | Hexafluoropropene | C6F6 | - | 5 |
| 180 | n - Hexane | C6H6 | 90 | 180 |
| 181 | Hyrazine | H4N2 | 0.05 | 0.1 |
| 182 | Hydrocarbons (1 - 10 C) |  | - | 300 |
| 183 | Hydrogen fluoride | HF | 0.1 | 0.5 |
| 184 | Hydrogen phosphide | H3P | 0.1 | 0.2 |
| 185 | Hydrogen selenide | H2Se | 0.03 | 0.1 |
| 186 | Hydrogene sulfide | H2S | 10 | 15 |
| 187 | Hydrogen cyanide | HCN | 0.3 | 0.6 |
| 188 | Hydroxydes (alkaline) (Alkali hydroxide) |  | 0.5 | 1 |
| 189 | Hydroquinone ( 1,4 - Dihydroxybenzene) | C6H6O2 | 0.5 | 1.5 |
| 190 | Iodomethane | CH3I | 1 | 2 |
| 191 | Iodoform | CHI3 | 3 | 10 |
| 192 | Iodine | I2 | 1 | 2 |
| 193 | Isopropyl glycidyl ether | (CH3)2C2H2O(CH3)2 | 240 | 360 |
| 194 | Isopropyl nitrate | C3H7NO2 | 20 | 40 |
| 195 | Potassium cyanide | KCN | 5 | 10 |
| 196 | Welding fumes |  | 5 | - |
| 197 | Petroleum gas (liquefied) |  | 1800 | 2250 |
| 198 | Zinc chloride | ZnCl2 | 1 | 2 |
| 199 | Zinc Chromate | CrO4Zn | 0.01 | 0.03 |
| 200 | Zinc fluoride | F2Zn | 0.2 | 1 |
| 201 | Zinc oxide (dust, fume) | ZnO | 5 | 10 |
| 202 | Zinc phosphide | P2Zn3 | - | 0.1 |
| 203 | Zinc stearate (inhalable dust) | Zn(C18H35O2)2 | 10 | 20 |
| 204 | Zinc stearate (respirable dust) | Zn(C18H35O2)2 | 5 | - |
| 205 | Zinc sulfide | ZnS | - | 5 |
| 206 | Camphor | C10H16O | 2 | 6 |
| 207 | Magnesium oxide | MgO | 5 | 10 |
| 208 | Malathion | C10H19O6PS2 | 5 | - |
| 209 | Manganese and compounds | Mn | 0.3 | 0.6 |
| 210 | Methallyl chloride | C4H7Cl | - | 0.3 |
| 211 | Methane thiol | CH4S | 1 | 2 |
| 212 | Methoxychlor | Cl3CCH(C6H4OCH3)2 | 10 | 20 |
| 213 | Methyl acrylate | CH2CHCOOCH3 | 20 | 40 |
| 214 | Metyl acrylonitrile | CH2C(CH3)CN | 3 | 9 |
| 215 | 2 - Methyl aziridine | C8H16N2O7 | 5 | - |
| 216 | Methylamine | CH5N | 5 | 24 |
| 217 | Methyl acetate | CH3COOCH3 | 100 | 250 |
| 218 | Methyl ethyl keton | C4H8O | 150 | 300 |
| 219 | 2 - Methyl furan | C5H6O | - | 1 |
| 220 | Methyl hydrazine | CH3NHNH2 | 0.08 | 0.35 |
| 221 | Methyl mercaptan | CH3SH | 1 | 2 |
| 222 | Methyl methacrylate | CH2C(CH3)COOCH3 | 50 | 150 |
| 223 | Methyl silicate | C4H12O4Si | - | 6 |
| 224 | Mevinphos | C7H13O6Pi | 0.1 | 0.3 |
| 225 | Monocrotophos | C7H14NO5P | 0.25 | - |
| 226 | Ferric salt (as Fe) |  | 1 | 2 |
| 227 | Carbon black | C | 3.5 | 7 |
| 228 | Naled | (CH3O)2P(O) OCHBrCBrCl2 | 3 | 6 |
| 229 | Naphthalene | C10H8 | 40 | 75 |
| 230 | Chlorinated naphthalenes |  | 0.2 | 0.6 |
| 231 | Sodium bisulfite | NaHSO3 | 5 | - |
| 232 | Sodium borate | Na2B4O7 | 1 | - |
| 233 | Sodium cyanide | NaCN | 5 | 10 |
| 234 | Sodium fluoroacetate | FCH2COONa | 0.05 | 0.1 |
| 235 | Sodium metabisulfite (Disodium pyrosulfite) | Na2S2O5 | 5 | - |
| 236 | Sodium azide | NaN3 | 0.2 | 0.3 |
| 237 | Neoprene | C4H5Cl | 10 | 30 |
| 238 | Aluminum and compounds | Al | 2 | 4 |
| 239 | Nicotine | C10H14N2 | 0.5 | 1 |
| 240 | Nickel and compounds (soluble) | Ni | 0.05 | 0.25 |
| 241 | Nickel monoxide | NiO, Ni2O3 | 0.1 | - |
| 242 | Nickel carbonyl | C4NiO4 | 0.01 | 0.02 |
| 243 | Nitrogen dioxide | NO2 và N2O4 | 5 | 10 |
| 244 | Nitrogen monoxide | NO | 10 | 20 |
| 245 | Nitrogene trifluoride | NF3 | 30 | 45 |
| 246 | Nitrobenzene | C6H5NO2 | 3 | 6 |
| 247 | 1- Nitrobutane | CH3(CH2)3NO2 | - | 30 |
| 248 | Nitro ethane | C2H5NO | 30 | - |
| 249 | Nitromethane | CH3NO2 | 30 | - |
| 250 | 1-Nitropropane | CH3(CH2)2NO2 | 30 | 60 |
| 251 | Nitrotoluene | CH3C6H4NO2 | 11 | 22 |
| 252 | Glycerol trinitrate (Nitroglycerine) | CH2NO3CHNO3CH2NO3 [C3H5(NO3)3] | 0.5 | 1 |
| 253 | 2-Nitropropane | CH3(CH2)2NO2 | 18 | - |
| 254 | Octane | C10H22 | 900 | 1,400 |
| 255 | Osmium tetroxide | OsO4 | 0.002 | 0.003 |
| 256 | Ozone | O3 | 0.1 | 0.2 |
| 257 | Paraquat | (CH3(C5H4N)2CH3).2Cl | 0.1 | 0.3 |
| 258 | Parathion | (C2H5O)2PSOC6H4NO2 | 0.05 | 0.1 |
| 259 | Pentaborane | B5H9 | 0.01 | 0.02 |
| 260 | Pentachlorophenol | C6Cl5OH | 0.2 | 0.4 |
| 261 | Perchloryl fluoride | ClO3F | 14 | 25 |
| 262 | Phenol | C6H5OH | 4 | 8 |
| 263 | Phenyl hydrazine | C6H5 NHNH2 | 1 | 2 |
| 264 | Phenyl isocxyanate | C7H5NO | 0.02 | 0.05 |
| 265 | Phenylene diamine | C6H8N2 | 0.1 | 0.2 |
| 266 | Phenyl phosphine | C6H7P | - | 0.25 |
| 267 | Phorate | (C2H5O)2P(S)SCH2S-C2H5 | 0.05 | 0.2 |
| 268 | Phosgene | COCl2 | 0.2 | 0.4 |
| 269 | Phosphine | PH3 | 0.1 | 0.2 |
| 270 | Phosphorus(White, yellow) | P4 | 0.03 | 0.1 |
| 271 | Phosphoruos oxy chloride | POCl3 | 0.6 | 1.2 |
| 272 | Phosphorus trichloride | PCl3 | 1 | 2 |
| 273 | Phosphorous pentachloride | PCl5 | 1 | 2 |
| 274 | Picloram (iso) |  | 10 | 20 |
| 275 | Propoxur | CH3NHCOOC6H4OCH(CH3)2 | 0.5 | 1.5 |
| 276 | n-Propylacetat | CH3COOCH2CH2CH3 | 200 | 600 |
| 277 | -Propiolactone | C3H4O2 | 1 | 2 |
| 278 | Propylenimine | C3H7N | - | 5 |
| 279 | Pyrenthrin | C21H28O3 | 5 | 10 |
| 280 | Pyridine | C5H5N | 5 | 10 |
| 281 | Quinone | C6H4O2 | 0.4 | 12 |
| 282 | Resorcinol (1,3 - Dihydroxybenze) | C6H6O2 | 45 | 90 |
| 283 | Allyl alcohol | CH2CHCH2OH | 3 | 6 |
| 284 | Ethanol | CH3(CH2)OH | 1,000 | 3,000 |
| 285 | Furful alcohol | C5H6O2 | 20 | 40 |
| 286 | Methanol | CH3OH | 50 | 100 |
| 287 | n - Amyl alcohol | CH3(CH2)4OH | 100 | 200 |
| 288 | Propanol | CH3(CH2)2OH | 350 | 600 |
| 289 | Propargyl alcohol | HCCCH2OH | 2 | 6 |
| 290 | Rotenone (Derris) | C23H22O6 | 5 | 10 |
| 291 | Paraffin wax |  | 1 | 6 |
| 292 | Ferric oxide (dust, fume) | Fe2O3 | 5 | 10 |
| 293 | Iron carbonyl | C5FeO5 | 0.08 | 0.1 |
| 294 | Selenium and compounds | Se | 0.1 | 1 |
| 295 | Selenium dioxide | O2Se | - | 0.1 |
| 296 | Stibine | SbH3 | 0.2 | 0.4 |
| 297 | Strychnine | C21H22N2O2 | 0.15 | 0.3 |
| 298 | Selenium hexafluoride | SeF6 | 0.2 | - |
| 299 | Silane | H2Si | 0.7 | 1.5 |
| 300 | Stearates |  | 10 | - |
| 301 | Styrene | C6H5CH CH2 | 85 | 420 |
| 302 | Sulfur chloride | S2Cl2 | 5 | 10 |
| 303 | Sulfur dioxide | SO2 | 5 | 10 |
| 304 | Sunfuryl fluoride | F2SO2 | 20 | 40 |
| 305 | Sulfur tetrafluoride | SF4 | 0.4 | 1 |
| 306 | Tellurium | Te | 0.01 | - |
| 307 | Tellurium hexafluoride | F6Te | 0.1 | - |
| 308 | Tetrachloroethylene | C2CL4 | 60 | - |
| 309 | 1,1,7,7 Tetrachloroheptane | C7H12Cl4 | - | 1 |
| 310 | Tetraethyl pyrophosphate | C8H20O7P2 | 0.05 | 0.2 |
| 311 | Tetralin | C10 H12 | 100 | 300 |
| 312 | Tetramethyl succinonitrile | (CH3)2C2(CN)2(CH3)2 | 3 | 6 |
| 313 | Tetranitromethane | CH3(NO2)4 | 8 | 24 |
| 314 | Tin (organic) | Sn | 0.1 | 0.2 |
| 315 | Tin (inorganic) | Sn | 1 | 2 |
| 316 | Tin oxide | SnO2 | 2 | - |
| 317 | Thionyl Chloride | Cl2OS | 5 | - |
| 318 | Benzenethiol | C6H6S | 2 | - |
| 319 | Mercury compounds (organic) | Hg | 0.01 | 0.03 |
| 320 | Titanium | Ti | 10 | - |
| 321 | Thiram | (CH3)2 (SCSN)2 (CH3)2 | 5 | 10 |
| 322 | Tobacco (dust) |  | 2 | 5 |
| 323 | Mercury and compounds (inorganic) | Hg | 0.02 | 0.04 |
| 324 | Titanium dioxide (respirable dust) | TiO2 | 5 | - |
| 325 | Titanium dioxide (inhalable dust) | TiO2 | 6 | 10 |
| 326 | Toluene | C6H5CH3 | 100 | 300 |
| 327 | Toluene diisocyanate | C9H6N2O2 | 0.04 | 0.07 |
| 328 | (m-, o-, p-) Toluidine | CH3C6H4NH2 | 0.5 | 1 |
| 329 | Tribromometan | CHBr3 | 5 | 15 |
| 330 | Tributyl phosphate | C12H27O4P | 2.5 | 5 |
| 331 | Trichloroethane | C2H3Cl3 | 10 | 20 |
| 332 | Trichloroethylene | C2HCl3 | 20 | 40 |
| 333 | Trinitrobenzene | C6H3(NO2)3 | - | 1.0 |
| 334 | Trichloro nitrobenzene | C6H2Cl3NO2 | - | 1.0 |
| 335 | 2, 4, 6 - Trinitrotoluene | CH3C6H2(NO2)3 | 0.1 | 0.2 |
| 336 | Tritolyl phosphate | C21H21O4P | 0.1 | 0.2 |
| 337 | Uranium and compounds | U | 0.2 | - |
| 338 | Vanadium penta oxide | V2O5 | 0.05 | 0.1 |
| 339 | Vanadium | V | 0.5 | 1.5 |
| 340 | Vinyl acetate | CH2CHOOCCH3 | 10 | 30 |
| 341 | Vinyl bromide | CH2CBr | 20 | 40 |
| 342 | Vinyl chloride | C2H3Cl | 1 | 5 |
| 343 | Vinyl cyclohexene dioxide (930) | C8H12O2 | 60 | 120 |
| 344 | Warfarine | C19H16O4 | 0.1 | 0.2 |
| 345 | Wofatox | C8H10NO5PS | 0.1 | 0.2 |
| 346 | Petrol (Petrol distillates, gazonline) |  | 300 | - |
| 347 | Cellulose (inhalable dust) |  | 10 | 20 |
| 348 | Cellulose (respirable dust) |  | 5 | - |
| 349 | Cesium hydroxide | CsOH | 2 | - |
| 350 | Cyanogene | NCCN | 4 | 20 |
| 351 | Xyanogene chloride | ClCN | 0.3 | 0.6 |
| 352 | Cyanides | CN(K, Na) | 0.3 | 0.6 |
| 353 | Cyclohexane | C6H12 | 500 | 1,000 |
| 354 | Cychlohexanol | C6H11OH | 100 | 200 |
| 355 | Xylene | C6H4(CH3)2 | 100 | 300 |
| 356 | Xylidine | (CH3)2C6H3NH2 | 5 | 10 |

Part 2:

FIVE (05) PRINCIPLES AND SEVEN (07) MEASUREMENTS OF LABOR HYGIENE

I. PRINCIPLE 1 – ERGONOMIC DESIGN OF LABOR SYSTEMS

1. Scope of regulation

The ergonomic principles for designing labor systems in order to create optimum work conditions, ensure the safety, comfort and human health, technical and economic efficiency.

2. Subjects of application: the labor systems in facilities that employ workers (production facilities, business establishments, offices…)

3. Definition:

The terms in these principles are construed as follows:

3.1. Working facilities: are every production facilities, business establishments, offices…

3.2. Labor system: including humans and labor equipment, working together during the work process, performing the labor duties at working areas, in labor environment under the compulsory conditions of the labor duties.

3.3. Labor duty: is an expected result of the labor system.

3.4. Labor equipment: tools, machinery, vehicles and other machinery, devices or components used in the labor system.

3.5. The labor process: the continuation in time and space of the mutual impacts of humans, labor equipment, materials, energy and information within the labor system.

3.6. Labor space: the acceptable capacity for one or many people in the labor system to fulfill the labor duty.

3.7. The labor environment: the cultural, social, biological, chemical and physical factors around a person within his/her working space.

3.8. Labor stress (or external burden): every labor condition and external requirement for the labor system that negatively affect the human psychology and/or physiology.

3.9. Labor anxiety (or internal reaction): are impacts of labor stress on a person depending on his/her personal characteristics and abilities.

3.10. Labor fatigue:

Are systemic or partial non-pathological manifestation of fatigue due to the labor anxiety that may totally be recovered after some rest.

4. General principles

4.1. Working space design and labor equipment

a. Designs related to the body sizes:

The designs of the working space and equipment must depend on the human body sizes and the labor process. The working space must be adapted to the workers.

b. Posture:

- The worker may alternate between standing and sitting postures. If the worker must choose one, the sitting posture is usually preferred. The standing posture may be required depending on the work process.

- The postures must not cause labor fatigue due to extensive static muscular tension. The postures are interchangeable.

c. Muscle endurance:

- The requirement of muscle strength must be compatible to the worker’s physical condition.

- The muscle groups must be strong enough to satisfy the physical requirements. If the physical requirements are overwhelming, the supportive energy sources must be supplemented during the labor process.

- The extensive static tension of a muscle group must be avoided

d. The body movements:

- The movements must be balanced. The movement is more preferred than extensive static positions.

- The movement that require high precision must not demand considerable muscle strain.

- The movement must be made and combined easily using compatible control equipment.

e. The signs, monitors and control panel.

- The signals and monitors must be selected, designed and set up appropriately for the human sensory features, in particular:

+ The features and quantity of the signals and monitors must be appropriate for the information characteristics.

+ For clear information reception in places with many monitors, the monitors must be placed in order to achieve clear, firm and quick orientation. They might be arranged by function or technical process or importance and use frequency of special information.

+ The features and designs of signals and monitors must ensure clear recognition. These are applicable to danger signals.

+ The extensive activities in which the observation and supervision prevail, the overloading or underloading impacts must be avoided by designing and arranging the signals and monitors.

f. Control panels:

- Kinds, designs and arrangement of the control panels corresponding to the control are carried out depending on the human characteristics including natural and conditioned reflexes.

- The movement or static position of the control panel must be chosen depending on the control, the anthropometry and biomechanics.

- The functions of control panels must be recognizable.

- If there are multiple control panels at the same place, they must be clearly set up in order to ensure safe and quick operation. This may be carried out similarly to that of the signals by grouping by functions of the process in which they are used etc.

- The emergency control panel must be safely covered in order to avoid accidental activation.

4.2. Labor environment designs

Depending on the labor system, the following measurement must be noticed:

- The workshop sizes (general layout, working space and traveling space) must be reasonable.

- The clean air must be regulated depending on the following factors:

+ The quantity of people in a room,

+ The demand for manual labor,

+ The workshop size (including the labor equipment)

+ The emission of pollutants in a room,

+ The thermal conditions

- The light must be sufficient

The lighting must ensure optimum visions for the required activities.  The following measurements must be noticed:

+ The luminance.

+ The colors.

+ The light distribution.

+ The unwanted reflection and glare.

+ The contrast between the color and the reflection.

+ The worker age.

- The room and labor equipment colors must be selected depending on their impacts on the reflection distribution, the structure and quality of the field of view, the safety color perception.

- The negative or irritable impacts of noise, including the noise from external sources in auditory work areas must be prevented.

- The vibration and impacts on humans must not exceed the limit in order to avoid physical harm, physiological reaction, sickness or sensorimotor disorder.

- The exposure of the workers to dangerous material and hazardous radiation must be avoided.

- For outdoor works, the workers must be appropriately protected from negative impacts of the climate, e.g. cold, heat, wind, rain resistance etc.

4.3. Labor process designs

- The labor process must be designed in order to protect human health and safety, create comfort and ease the jobs, especially by avoid overload and underload. The overload and underload due to crossing the upper and lower limit of the mental and physical function scale. For example:

+ The physical burden and sensory burden that cause fatigue.

+ The underload burden or labor monotony may reduce vigilance.

- Apart from the above factor, the mental and physical stress also depend on the contents and the recurrence of the tasks and the control of humans throughout the work process.

- Taking measures for improving the work process quality. For example:

+ Only one worker performs a number of consecutive tasks of the same work instead of a few workers (work extension).

+ Only one worker performs a number of consecutive tasks of the different works instead of a few workers (work variety).

+ Changing works. For example: alternating the voluntary works among the workers on the same assembly line or in one autonomous team.

+ Organized or unorganized breaks.

- During the implementation of the above measures, it is required to pay attention to:

+ The change in the insomnia and the work ability in day and night.

+ The difference in work ability among the workers and the variance in ages.

+ The personal abilities.

II. PRINCIPLE 2 – ERGONOMIC DESIGN OF WORKING LOCATIONS

1. Scope of regulation

The ergonomic principles for designing working positions in every business line in order to create optimum work conditions, ensure the safety, comfort and human health, technical and economic efficiency.

2. Subjects of application: every working position

3. Definition:

The terms in these principles are construed as follows:

- Working position: is a space where the technical equipment is equipped for one person or a group of people to work on a job or a phase.

- The reaching zone of the motion range is part of the working position, limited by the arc created by a stretched arm’s movement around the shoulder joint.

- The easy reaching zone of the motion range is part of the working position, limited by the arc created by a stretch arm’s movement around the shoulder joint (where the control equipment is regularly used).

- The optimum reaching zone of motion range is part of the working position, limited by the arc created by a stretch arm’s movement around the elbow joint (where the control equipment is always used).

4. General principles of ergonomics

- The working position must be adapted to each kind of work, to the ability, to the mental and physical characteristics of the worker.

- The working position must be designed on the basis of the analysis of the human work process with particular equipment, basing on the anthropometrical measurements, the mental and physical characteristics of the worker and the assessment of hygienic conditions of the work.

- The working area arrangement includes: calculating the sizes basing on the anthropometrical measurements, selecting the appropriate working zone, surface, comfortable working posture and reasonably designing, arranging the equipment.

- The machinery and equipment must be suitable for the mental and physical characteristics of the worker (especially the anthropometrical and biomechanical characteristics).

- Arranging labor in the production premises in an optimum way including safe and adequate passages.

- The light (artificial or natural) must be sufficient for both ordinary works and machinery maintenance.

- The noise and vibration from the working positions or other sources must not exceed the acceptable standards.

- The necessary measures for protecting workers from the impact of dangerous and toxic factors (physical, chemical, biological, psychological and physiological factors) during the production must be taken.

- The measures for preventing and reducing workers’ fatigue, psychological stress and other negative impacts must be taken.

5. Principles for working position arrangement:

- The working location arrangement must ensure that the task is performed within the accessible zone of the motion range.

- There are 3 kinds of accessible zones of the motion range.

* Reaching zone

* Easy reaching zone

* Optimum reaching zone

- The space for legs and feet while sitting must be sufficient.

- The requirements for the vision from the working location must be satisfied.

- The information display zones must be optimized (display devices, signboards, signals…) for the worker to receive information efficiently.

- The height of working surfaces, the distance from eyes to the observed objects, the view angle, footrest space must be sufficient.

- The size and height of the chair must be convenient for changing the working posture. The chair must not be to deep. The distance from the chair surface to the table surface must not be lower than 270 - 300mm.

III. PRINCIPLE 3 – ERGONOMIC DESIGN OF MACHINERY AND TOOLS

1. Scope of application

The ergonomic principles for designing machinery and tools in every business line is to design optimum machinery and tools in order to ensure the safety, comfort and human health, technical and economic efficiency.

2. Subjects of application: every working machinery and tools.

3. The principles

- Depending on the variance in body size when systemically or partially move the body.

- Depending on the motion range of the joints. The comfortable angles of the body.

- Depending on the required forces on the control devices.

- The principle of movement limitation in order to ensure comfortable postures and optimum working zones.

- The requirements for hygiene and appearance (shape, paint color…) must be satisfied.

- The principle of using anthropometry figures: after using the tools, the subject shall select the anthropometry figures as the basis for calculating the sizes of machinery and tools, the percentage of people that concur with the tool and machinery design.

IV. MEASUREMENT 4 – HEIGHT OF WORK SURFACES

1. Scope of regulation: principles of work surface height design.

2. Subjects of application: every working position

3. The principles

|  | Work characteristics | Height of working zone |
| --- | --- | --- |
| 1 2 3 4 5 | Works that demand precise observation Works that need handwork Works that need free hand movement Works with heavy material (for standing position only) Works with various demands | 10 - 20 cm above the elbow 5 - 7cm above the elbow Slightly under the elbow 10 - 30cm under the elbow Determined by the work that demands the most |

V. PRINCIPLE 5 – WORKING POSITIONS WITH COMPUTERS

1. Scope of application: the basic principles of designing working positions with computers.

2. Subjects of application: every working positions with desktop computer.

3. The principles

3.1. Working positions

- The working position must be designed suitably for the worker. Ideally the position should be adjusted to suit each worker. In case the position cannot be adjusted, the design must be based on the anthropometry (5% and 95%).

- The adjustable working surface height should range from 65 - 75cm. If the height is not adjustable: 70 cm

- The height of the monitor and keyboard must be independently adjustable.

- The minimum distance between two workers is 1m (from the center of the working position).

3.2. Working surface:

- The working surface must not be glaring and reflective, and must be spacious enough to place necessary stuff such as the keyboard, mouse and document for the worker’s comfort.

- The document holder (if any) must be firm and placed at positions that do not cause the user to make inconvenient head and eye movements.

- If the use of computers is primary, it must be placed in front of the operator. If the use of computers is secondary, it must be placed on the left, if the operator is right-handed and vice versa.

3.3. Chair and backrest:

- The chair height must be adjustable from 35-50 cm and rotatable.

- The chair must be firm. The chair must not be covered by synthetic waterproof material.

- The seat depth is 38- 43 cm, at least 45 cm in width, edgeless. The tilt being 0 - 100 that can handle the body weight on the buttock (not on the thigh).

- The performance on the keyboard must not be hindered when the arm is rested.

- For mobile chairs, the 5 castors must be fixed on the chair.

- The backrest must be adjustable that can handle the back (hip).

3.4. Footrest:

- There must be space for the operator’s feet to be comfortable.

- The overly tall chairs must have footrests. The tilt angle of the footrest is approximately 300 with non-slip surface.

3.5. The operator’s posture:

- The operator must sit comfortably with the back rested and feet on the floor or the footrest. The elbow angle is approximately 900, the angle between the body and the thigh is from 90-1200.

- The operator should avoid rigid sitting posture for a long time but may change the position, stand, stretch or walk around if feel tired.

3.6. View angle and visions:

- The best view angle is between 10-300 below the horizontal line of sight of the operator. The upper side of the monitor must not be higher than the eye-level. The angle between the ray from the lower side of the monitor and the horizontal line of sight must not exceed 400.

- The appropriate vision is not shorter than 50 cm.

3.7. Glare prevention and lighting

- The general light intensity: 300 - 700 lux For places with special visual requirements, the intensity may reach 700 - 1,000 lux. Partial lighting might be used for document reading with lampshade for glare prevention.

- Diminishing the reflection and glare by properly placing the light sources, not using reflective surfaces and items...

- Paying attention to the light sources when arranging computers so that the monitor would not reflect the light. Arranging computer so that the window does not face the monitor or its back. The computers should be placed at intersections of the light sources overhead rather than right below them.

- The monitor must be covered with anti-glare coat. If the anti-glare coat is not available, the monitor must be equipped with anti-reflection equipment in order to prevent glare from reflection. Such equipment must not reduce the definition of graphics and text. Only use the anti-glare filter when other solutions are not available.

- The wall color must be elegant with low reflection level (non-glossy). The colors of surrounding equipment must also be non-glossy or dark in order to avoid reflection of light sources. Avoid using reflective, shimmering or glossy surfaces at workplaces.

3.8. Environment

- The working room temperature is from 23 - 250C, the maximum relative humidity is 75%.

- The minimum ventilation volume is 13 m3/hour/person. The wind speed must not exceed 0.5 m/second.

- The noise must not exceed 55 dBA.

3.9. Breaks

- After every hour of continuous work with computer, a short break to rest or doing light works not related to the monitor is recommended It is best to leave the computer during this time.

- It is better to exercise the muscles or eyes during this time.

- This time is not included in the break time.

VI.  V. MEASUREMENT 1 – WORKING POSITIONS WITH COMPUTERS

1. Scope of application

The basic measurements of designing working positions with computers basing on the basic principles stated above.

2. Subjects of application: the working positions with desktop computer.

3. Measurements

| No. | Norm | Size |
| --- | --- | --- |
| 1 | Table, chair, posture Table height: - Adjustable (cm) - Non-adjustable (cm) - Chair height (adjustable) (cm) Seat depth (cm) Minimum seat width (cm) Seat slope toward the backrest (degree) Footrest space (cm) Footrest slop (degree) Elbow angle (degree) Body – thigh angle (degree) View angle (below the horizontal line of sight) (degree) Vision (cm) | 65 - 70 70 35 - 50 38 - 43 45 0 - 10 19 30 85 - 95 90 - 120 10 - 30 >50 |
| 2 | Environment - General lighting (lux): - normal - Special visual requirements - Temperature (0C) - Maximum humidity (%) - Minimum ventilation - Wind speed(m/second) - Noise (dBA) | 300 -700 700- 1,000 23 - 25 75 13 m3/hour/person Not exceeding 0.5 Not exceeding 55 |
| 3 | Continuous working time | 1-2 hours |

VII. MEASUREMENTS 2- – HEIGHT OF WORKING SURFACES

1. Scope of regulation

basic measurements of working surface height.

2. Subjects of application: working positions.

3. Measurements:

| Posture | Kind of work | Height of working surface (cm) |  |  |
| --- | --- | --- | --- | --- |
|  |  | Male | Female | Male and female |
| Standing | Light | 88 - 102 | 85 - 97 | 86 - 99 |
|  | Medium | 80 - 94 | 77 - 89 | 78 - 91 |
|  | Heavy | 74 - 88 | 71 - 83 | 72 - 85 |
| Sitting | High precision | 73 - 86 | 70 - 83 | 70 - 83 |
|  | Precision | 65 - 78 | 62 - 75 | 64 - 77 |
|  | Light works without high precision | 60 - 73 | 57 - 70 | 59 - 72 |

VIII. MEASUREMENTS 3 – VIEW DISTANCE FROM EYES TO THINGS

1. Scope of regulation

The measurements of view distance from eyes to the working objects.

2. Subjects of application: working positions

3. Measurements

| No. | Work characteristic | View distance (from eyes to things) |
| --- | --- | --- |
| 1 2 3 4 | Works demanding extreme precisions (small part assembly…) Works demanding high precision (drawing, sewing, seaming…) Works demanding precision and medium precision (reading, lathe…) Works demanding little precision | 12 - 25cm 25 - 35cm 35 - 50cm Over 50cm |

IX. MEASUREMENTS 2 – VIEW ANGLE

1. Scope of regulation

The measurements of view angle in working position design in order to create comfort and productivity.

2. Subjects of application: working positions.

3. The measurement of view angle with the horizontal line of sight  00

| No. | Working posture | View angle |
| --- | --- | --- |
| 1 2 | Leaning backward (e.g. working in control rooms) Leaning forward (e.g. – working at tables) | 150 450 |

* One side of a view angle is the horizontal line of sight.

* The object of work under regular observation must be put at the front center field of view

X. SPECIFICATONS 5 – FOOTREST SPACE

1. Scope of regulation

The measurements of footrest space in working position design in order to create comfort and productivity.

2. Subjects of application: working positions.

3. Measurements:

| No. | Working posture | Footrest space |
| --- | --- | --- |
| 1 2 3 | Sitting positions: Width Depth at knee-level Depth at floor-level Standing positions: Depth for feet Height for feet The free space behind the standing worker | 60 cm  45 65  15 cm  15 cm 90 cm |

XI. MEASUREMENTS 6 – LIFTING HEIGHT

1. Scope of regulation

The measurements of height from the floor to the person lifting in order to create comfort and avoid vocational risks.

2. Subjects of application: the workers that lift heavy things.

3. Definition`

The terms in these standards are construed as follows:

- Normal lifting height: within the range from the elbow joint to the shoulder joint.

- Low lifting height: under the elbow joint.

4. Measurements

| Level | Normal lifting height |  |  |  | Low lifting height |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Distance to the handle (cm) |  |  |  | Distance to the handle (cm) |  |  |  |
|  | < 30 | 30-50 | 50-70 | >70 | < 30 | 30-50 | 50-70 | >70 |
|  | Lifting weight (kg) |  |  |  | Lifting weight (kg) |  |  |  |
| 1 | Heavy things easily lifted by machines |  |  |  |  |  |  |  |
| 2 | < 18 | < 10 | < 8 | < 5 | < 13 | < 8 | < 5 | < 4 |
| 3 | 18-34 | 10-19 | 8-13 | 6-11 | 13-23 | 8-13 | 5-9 | 4-7 |
| 4 | 35-55 | 20-30 | 14-21 | 12-28 | 24-25 | 14-21 | 10-15 | 8-13 |
| 5 | >55 | >30 | 21 | >18 | >35 | >21 | >15 | >8 |

XII. MEASUREMENTS 7: PHYSIOLOGICAL MEASUREMENTS OF THERMAL STRAIN – LIMIT VALUES

1. Scope of regulation: The limit values of physiological measurements of thermal strain including the risks to health of healthy workers, the adaptability to different technologies to detect such risks.

2. Subjects of application: workers at every facility working in hot or cold environment.

3. Reference standard: ISO 9886

4. Physiological specifications of thermal strain

4.1. Body core temperature

The body core temperature must not differ from the values in section 4.1.1 and 4.1.2.

4.1.1. Hot environment

The limit values depend on the core temperature increase and the used measurements.

The core temperature must not increase more than 10C (or not exceed 380C) in the following cases;

- The core temperature is taken many times, regardless of the techniques.

- When other physiological measurements are not taken.

In other conditions, especially when the esophagus temperature is continuously monitored concurrently with the heart rate, the limit may be raised such as increasing 1.40C or reaching 38.50C.

The increase of temperature over 38.50C might be tolerable when the following conditions are satisfied:

a. The subject has been given medical examination.

b. The subject has adapted to the heat by repeatedly exposing to such environment when performing special duties.

c. Under constant medical supervision and means of first-aid are ready.

d. The esophagus temperature is continuously monitored.

e. Other physiological measurements are concurrently monitored – especially the heart rate

f. The exposure might be immediately suspended when the intolerable symptoms appear such as fatigue, vertigo, nausea

g. The workers are entitled to leave the workplace when they want.

The core temperature must not exceed 390C.

4.1.2. Cold  environment:

In cold environments, only the measurements of esophagus temperature (tes), rectum temperaturer (tre) and abdomen temperature are suitable. The lower limit for these temperatures is 360C. Conditions of application:

a. When these temperatures are monitored from time to time.

b. When the exposure is repeated in a day.

c. In some rare conditions, the lower temperature might be tolerable briefly.

d. The subject has been given medical examination

e. The skin temperature is concurrently monitored and the acceptable limit is noticed.

f. The workers are entitled to leave the workplace when they want.

4.2. The skin temperature limit values:

For the previously mentioned reasons, the below limits are only related to the pain threshold.

In hot environments, the maximum partial skin temperature is 400C. In cold environments: 200C for forehead skin, 100C for limb tip temperature (especially finger tips and toe tips).

4.3. Heart rate (HR):

The heart rate increase (HRT) by thermal strain is 33 beats for each degree increased of the core temperature. However, the heart reaction to heat varies from person to person. Therefore, in case the HR is the only physiological measurement monitored, the upper limit of HRT  around 30 beats/minute would be reasonable. In circumstances that the thermal strain might be high, it must be measured simultaneously with the core temperature. Moreover, there must be means to monitor the actual heart rate throughout the exposure.

The limited heart rate at workplaces must not exceed the maximum limit minus 20 beats/minute. Ideally, these values should be calculated by personal test. If such test cannot be carried out, the values could be approximated using the following formula:

HRL  0.85 A (A is the age in year).

According to the maximum limit of the core temperature being 390C, the maximum limit of the heart rate increase from the initial temperature may reach 60 beat/minute. This may be applicable to the similar situations, especially under medical supervision and constant monitoring.

4.4. Weight loss:

The limit value of weight loss is 800g for adapted workers and 1300g for unadapted ones, proportionally to the water loss being 3250g or 5200g in case the water intake is 75% of the water loss.

These values refer to subjects with 1.8 m2 of skin and may be applicable to a particular subject by proportionally multiplied the skin area ADu with the reference skin area being 1.8 m2

| Limit values | Unadapted person |  | Adapted person |  |
| --- | --- | --- | --- | --- |
|  | Caution | Danger | Caution | Danger |
| Sweat level Idle: M<65W/m2 SWmax W/m2 g/hour Working: M>65W/m2 SWmax W/m2 g/hour | 100 250 200 520 | 150 390 250 650 | 200 520 300 780 | 300 780 400 1040 |
| Maximum water loss DmaxW.h/m2 g | 1 000 2 600 | 1 250 3 250 | 1 500 3 900 | 2 000 5 200 |
| Notes: W  watt-hour  hour g  gram |  |  |  |  |

Notes:   * M  energy metabolism level

* SW sweat weight

TABLE OF CONTENTS

Part 1: Twenty one (21) standards of labor hygiene

I. Standards of hygienic amenities

II. Standards of hygienic distance

III. Manual labor – Standards of task classification by energy consumption classification

IV. Manual labor – Standards of task classification by heart rate

V. Carrying standard – Limited weight

VI. Lighting standards

VII. Microclimate standards

VIII. Standards of silicon dust

IX. Standards of non-silicon dust

X. Standards of cotton dust

XI. Standards of asbestos dust

XII. Standards of noise

XIII. Standards of vibration

XIV. Standards of static magnetic field - Magnetic flux density

XV. Standards of low-frequency magnetic field - magnetic flux density

XVI. Standards of intensity of low-frequency electromagnetic field and static electric field

XVII. Standards of intensity of electromagnetic field from 30kHz - 300GHz

XVIII. Ultraviolet radiation – Acceptable limit

XIX. Standards of radioactivity

XX. X-ray radiation – Acceptable limit

XXI. Chemicals – Acceptable limit in the working air

Part 2: Five (05) principles and seven (07) measurements of labor hygiene

I. Principle 1 – Ergonomic design of labor systems

II. Principle 2 – Ergonomic design of labor positions

III. Principle 3 – Ergonomic design of machinery and tools

IV. Principle 4 – Working area layout

V. Principle 5 – Working position with computers

VI. Measurement 1 – Working position with computers

VII. Measurement 2 – Height of work surfaces

VIII. Measurement 3 – Distance from eyes to things

IX. Measurement 4 - View angle

X. Measurement 5 – Footrest

XI. Measurement 6 – Lifting height

XII. Measurement 7 – Physiological measurement of thermal strain - Limit values